## Input
Service Pro 2026 (Version 26.0A) - Single Family Optional Calculation Method - Copyright 2025 - Durand & Associates | [8 empty] | 0 | MAIN | 0
[8 empty] | 1-1 1/4'' EMT |  | PANEL
GENERAL INFORMATION |  |  |  |  | VOLTAGE DROP CALCS | YES |  |  |  |  | 2008 |  |  |  |  | NONE | EMT
| PROJECT NAME |  | SAMPLE |  | HIGH VOLTAGE | 240 |  |  | HIGH VOLTAGE | 240 | [5 empty] | 1" | RIGID
| ADDRESS |  | 123 MAIN |  | LOW VOLTAGE | 120 |  |  | LOW VOLTAGE | 120 | [5 empty] | 1 1/4" | IMC
| CITY/STATE/ZIP |  | FOLSOM, CA 95630 |  | FAULT CURRENT CALCS | YES |  |  | PHASE | 1 | [5 empty] | 1 1/2" | PVC
| CODE YEAR |  | 2008 |  | AVAILABLE FAULT CURRENT | 22000 |  | 0 | [7 empty] | 2"
| CALCULATION METHODE |  | OPTIONAL |  | PANEL NAME | MAIN PANEL |  | 0 |  | MAIN PANEL | [5 empty] | 2 1/2"
SERVICE FEEDER |  |  |  |  | PHASE | 1 |  | 0 | [7 empty] | 3"
| OVERHEAD / UNDERGROUND |  | UNDERGROUND |  | TOTAL SQUARE FOOTAGE | 1500 |  | 0 | [7 empty] | 3 1/2"
| METER-MAIN.PANEL |  | METER |  | APPLIANCE CIRCUITS | 2 |  | 0 | [7 empty] | 4"
| MAIN-PANEL |  | MAIN PANEL |  | LAUNDRY CIRCUITS | 1 |  | 0
| CONDUIT SIZE |  | 3" |  |  |  |  | 0 | [9 empty] | 3"
| CONDUIT TYPE |  | PVC |  | SERVICE RISER | FEEDER |  | 0
FEEDER | [5 empty] | 1-1 1/4'' EMT |  | 0 | 0 | 0 | [7 empty] | PVC
| FEEDER TYPE |  | CONDUIT |  |  | 2-#1 THHN AL |  | 0 | 1 | 10 | ' | 110'
| LENGTH |  | 10 |  | DEMO VERSION | 1-#4 THHN AL (N) |  | 0 | [9 empty] | 3" PVC
| WIRE CU/AL |  | AL |  | ORANGE CELLS | 1-#4 AL GND |  | 0
| WIRE TEMP |  | 75 |  | ARE PROTECTED |  |  | 0
| MINIMUM AMPS |  | 0 |  |  |  |  | 0
| % FACTOR |  | 0 |  |  | AFC AT THIS PANEL |  | 0
| GROUND WIRE Y/N |  | YES |  |  | 15,774 CLC |  | 0
| SELECT WIRE TYPE |  | THHN |  |  |  |  | 0
| CONDUIT TYPE |  | EMT |  |  |  |  | 0
| VOLTAGE DROP % FACTOR |  | 0 |  |  |  |  | 0
SUBPANELS | [7 empty] | 0
| NUMBER OF SUBPANELS |  | 6
[7 empty] | SP1 | 0 | [5 empty] | UPDATE | ERROR
MAJOR APPLIANCES | [7 empty] | 0 |  |  |  |  | SP1 | 0 | 0
| DESCRIPTION |  | QTY | KVA (EA) |  |  |  | 0 | 0 | 0
| RANGE(S) & OVEN(S) |  | 1 | 12 |  | MAIN PANEL | SP2 | 0 | 0 | 0 | 0
| CLOTHES DRYER(S) |  | 1 | 5.5 |  |  |  | 0 | 0 | 0 |  |  | SP2 | 0 | 0
| WATER HEATER(S) |  | 1 | 4.5 |  |  |  | 0
SP3
BUILT-IN APPLIANCES ( 120 VOLT ) | [12 empty] | SP3 | 0 | 0
|  | DESCRIPTION | QTY | AMPS |  |  |  | 0 | 0 | 0
|  | FURNACE | 1 | 7.2 |  |  | SP4 | 0 | 0 | 0
|  | DISPOSAL | 1 | 6.5 |  |  |  | 0 | 0 | 0 |  |  | SP4 | 0 | 0
|  | DISHWASHER | 1 | 11.2 |  |  |  | 0 | 0 | 0
|  | MIRCOWAVE | 1 | 9 |  |  | SP5 | 0 | 0 | 0
|  | CENTRAL VAC | 1 | 12 |  |  |  | 0 | 0 | 0 |  |  | SP5 | 0 | 0
[8 empty] | 0 | 0 | 0
[7 empty] | SP6 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 |  |  | SP6 | 0 | 0
[8 empty] | 0 | 0 | 0
[8 empty] | 0 | [5 empty] | 0 | 0
HEATING/COOLING | [7 empty] | 0
0
1. | ENTER 100% OF THE NAMEPLATE RATING(S) OF THE AIR CONDITIONING AND |  |  |  |  | ENTER KVA |  | 0
| COOLING EQUIPMENT. |  |  |  |  | 4 |  | 0
0
2. | ENTER 100% OF THE NAMEPLATE RATING(S) OF THE HEAT PUMP WHEN THE HEAT PUMP |  |  |  |  | ENTER KVA
| IS USED WITHOUT ANY SUPPLEMENTAL ELECTRIC HEATING. |  |  |  |  | 0 |  | 0
3. | ENTER 100% OF THE NAMEPLATE RATING(S) IN KVA OF THE HEAT PUMP |  |  |  |  | ENTER KVA
| COMPRESSOR. |  |  |  |  | 0 |  | 0
| ENTER 100% OF THE SUPPLEMENTARY ELECTRIC HEAT USED WITH THE HEAT PUMP. |  |  |  |  | ENTER KVA
| NOTE: PROGRAM WILL AUTOMATICALLY ADJUST THIS AMOUNT TO 65%. |  |  |  |  | 0 |  | 0
4. | ENTER 100% OF THE NAMEPLATE RATING(S) OF ELECTRIC SPACE HEATING IF LESS THAN |  |  |  |  | ENTER KVA
| FOUR SEPARATELY CONTROLLED UNITS. |  |  |  |  | 0 |  | 0
NOTE: PROGRAM WILL AUTOMATICALLY ADJUST THIS AMOUNT TO 65%.
[6 empty] | 0 |  | 0
5. | ENTER 100% OF THE NAMEPLATE RATING(S) OF ELECTRIC SPACE HEATING IF FOUR OR |  |  |  |  | ENTER KVA
| MORE SEPARATELY CONTROLLED UNITS. |  |  |  |  | 0 |  | 0
NOTE: PROGRAM WILL AUTOMATICALLY ADJUST THIS AMOUNT TO 40%.
6. | ENTER 100% OF THE NAMEPLATE RATING(S) OF ELECTRIC THERMAL STORAGE |  |  |  |  | ENTER KVA
| AND OTHER HEATING SYSTEMS WHERE THE USUAL LOAD IS EXPECTED TO BE CONTINUOUS |  |  |  |  | 0 |  | 0
AT THE FULL NAMEPLATE VALUE. SYSTEMS QUALIFYING UNDER THIS SELECTION SHALL NOT
BE CALCULATED UNDER ANY OTHER SELECTION IN 220.82(C).
MISC. 120 VOLT LOADS |  |  |  | AMPS |  |  |  | 0
|  | DESCRIPTION | QTY. | EACH |  |  |  |  | 0 | 0 | 0
| 1 | [6 empty] | 0 | 0 | 0 | 0
| 2 | [6 empty] | 0 | 0 | 0 | 0
| 3 | [6 empty] | 0 | 0 | 0 | 0
| 4 | [6 empty] | 0 | 0 | 0 | 0
| 5 | [6 empty] | 0 | 0 | 0 | 0
| 6 | [6 empty] | 0 | 0 | 0 | 0
| 7 | [6 empty] | 0 | 0 | 0 | 0
| 8 | [6 empty] | 0 | 0 | 0 | 0
| 9 | [6 empty] | 0 | 0 | 0 | 0
| 10 | [6 empty] | 0 | 0 | 0 | 0
| 11 | [6 empty] | 0 | 0 | 0 | 0
| 12 | [6 empty] | 0 | 0 | 0 | 0
| 13 | [6 empty] | 0 | 0 | 0 | 0
| 14 | [6 empty] | 0 | 0 | 0 | 0
| 15 | [6 empty] | 0 | 0 | 0 | 0
| 16 | [6 empty] | 0 | 0 | 0 | 0
| 17 | [6 empty] | 0 | 0 | 0 | 0
| 18 | [6 empty] | 0 | 0 | 0 | 0
| 19 | [6 empty] | 0 | 0 | 0 | 0
| 20 | [6 empty] | 0 | 0 | 0 | 0
| 21 | [6 empty] | 0 | 0 | 0 | 0
| 22 | [6 empty] | 0 | 0 | 0 | 0
| 23 | [6 empty] | 0 | 0 | 0 | 0
| 24 | [6 empty] | 0
MISC. 208 OR 240 VOLT LOADS |  |  |  | AMPS
|  | DESCRIPTION | QTY. | EACH |  |  |  |  | 0 | 0 | 0 | 0
| 1 | PUMP | 1 | 16 | 3Y |  |  | 0 | 0 | 0 | 0 | 0
| 2 |  |  |  | 3Y |  |  | 0 | 0 | 0 | 0 | 0
| 3 |  |  |  | 3Y |  |  | 0 | 0 | 0 | 0 | 0
| 4 |  |  |  | 3Y |  |  | 0 | 0 | 0 | 0 | 0
| 5 |  |  |  | 3Y |  |  | 0 | 0 | 0 | 0 | 0
| 6 |  |  |  | 3Y |  |  | 0 | 0 | 0 | 0 | 0
| 7 |  |  |  | 3Y |  |  | 0 | 0 | 0 | 0 | 0
| 8 |  |  |  | 3Y |  |  | 0 | 0 | 0 | 0 | 0
| 9 |  |  |  | 3Y |  |  | 0 | 0 | 0 | 0 | 0
| 10 |  |  |  | 3Y |  |  | 0
Service Pro 2026 (Version 26.0A) - Single Family Optional Calculation Method - Copyright 2025 - Durand & Associates
0

## Calcs
[9 empty] | CODE YEAR | 2008 | [10 empty] | (
SINGLE FAMILY SERVICE LOAD CALCULATIONS |  | PROJECT NAME |  | SAMPLE |  |  | 0 |  | OPT/STD | OPTIONAL |  | TOTAL SQ FOOTAGE ( | [6 empty] | MISC LOADS
BASED ON THE 2008 NEC SECTION 220.82 |  | PANEL NAME |  | MAIN PANEL |  |  | 0 |  |  |  |  | APPLIANCE CIRCUITS ( | [5 empty] | 1 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | WATER HEATER | ( | 1 | X | 4500 | VA X |  |  | 1 | ) = | 4500 | VA
[7 empty] | 0 |  |  |  |  | LAUNDRY CIRCUITS ( | [5 empty] | 2 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | FURNACE | ( | 1 | X | 7.2 | X | 120 | X | 1 | ) = | 864 | VA
GENERAL LOADS NEC 220.82(B) |  | HEATING & COOLING LOADS - NEC 220.82(C) | [15 empty] | 3 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | DISPOSAL | ( | 1 | X | 6.5 | X | 120 | X | 1 | ) = | 780 | VA
TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = | 4500 | (1) AC LOAD ( 4,000 VA X 100% ) = 4,000 VA |  |  | < < LARGEST |  |  | 1,500 | SQ FT X 3 VA ) = |  |  | TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = | [5 empty] | 4 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | RANGES | 1 | [5 empty] | DISHWASHER | ( | 1 | X | 11.2 | X | 120 | X | 1 | ) = | 1344 | VA
APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = | 3000 | (2) HEAT PUMPS NO SUPP ( 0 VA X 100% ) = 0 VA | [5 empty] | 2 | X 1,500 VA ) = |  |  | APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = | [5 empty] | 5 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | SIZE | 12 | [5 empty] | MIRCOWAVE | ( | 1 | X | 9 | X | 120 | X | 1 | ) = | 1080 | VA
LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = | 1500 | (3) HEAT PUMPS ( 0 VA X 100% ) = 0 VA | [5 empty] | 1 | X 1,500 VA ) = |  |  | LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = | [5 empty] | 6 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PHASE | 1 | [5 empty] | CENTRAL VAC | ( | 1 | X | 12 | X | 120 | X | 1 | ) = | 1440 | VA
|  | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = 0 VA | [5 empty] | 1 | X | 12,000 | VA = | 1 X 12,000 VA = | [5 empty] | 7 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | CEILING | 2 | [6 empty] | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | (4) ELECTRIC SPACE ( 0 VA X 65% ) = 0 VA | [5 empty] | 1 | X | 5,500 | VA = | 1 X 5,500 VA = | [5 empty] | 8 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | LESS THAN FOUR SEPARATELY CONTROLLED UNITS. | [5 empty] | 1 | X | 4,500 | VA ) = | WATER HEATERS ( 1 X 4,500 VA ) = | [5 empty] | 9 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | RANGE ( | 1 | RANGE X | 12000 | VA ) = | 12000 |  |  | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | (5) SPACE HEATING ( 0 VA X 40% ) = 0 VA | [15 empty] | 10 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | RANGE ( | 1 | RANGE X | 12,000 | VA ) = |  | RANGE ( 1 RANGE X 12,000 VA ) = |  | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | MORE THAN FOUR SEPARATELY CONTROLLED UNITS. | [9 empty] | WATER HEATERS ( | [5 empty] | 11 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | (6) SPACE HEATING (0 VA X 100% ) = 0 VA | [15 empty] | 12 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PER PHASE DEMAND ( | 12000 | VA ÷ 2 ) = | 6000 | VA |  |  |  |  | 1
RANGE ( 1 RANGE X 12,000 VA ) = | 12000 | CONTINUOUS AT THE FULL NAMEPLATE VALUE. | [15 empty] | 13 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PER PHASE DEMAND ( | 12,000 | VA ÷ 2 ) = | 6,000 | VA
|  | LARGEST HEATING OR COOLING LOAD |  |  | 4000 | [12 empty] | 14 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | WATER HEATER | ( | 1 | X | 4,500 | VA |  |  |  | ) = | 4,500 | VA | WATER HEATER ( 1 X 4,500 VA ) =
[8 empty] | MISC LOADS | 3840 | [8 empty] | 15 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 6000 | VA X 3 ) = |  |  |  |  | FURNACE | ( | 1 | X | 7.2 | A X | 120 | V |  | ) = | 864 | VA | FURNACE ( 1 X 7.2 A X 120 V ) =
|  | NEUTRAL LOAD NEC 220.61 | [15 empty] | 16 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 6,000 | VA X 3 ) = |  |  |  |  | DISPOSAL | ( | 1 | X | 6.5 | A X | 120 | V |  | ) = | 780 | VA | DISPOSAL ( 1 X 6.5 A X 120 V ) =
|  | TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = |  |  | 4500 | [12 empty] | 17 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | DISHWASHER | ( | 1 | X | 11.2 | A X | 120 | V |  | ) = | 1,344 | VA | DISHWASHER ( 1 X 11.2 A X 120 V ) =
|  | APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = |  |  | 3000 | [12 empty] | 18 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | MIRCOWAVE | ( | 1 | X | 9.0 | A X | 120 | V |  | ) = | 1,080 | VA | MIRCOWAVE ( 1 X 9.0 A X 120 V ) =
DRYER ( 1 DRYER X 5,500 VA ) = | 5500 | LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = |  |  | 1500 | [12 empty] | 19 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | CENTRAL VAC | ( | 1 | X | 12.0 | A X | 120 | V |  | ) = | 1,440 | VA | CENTRAL VAC ( 1 X 12.0 A X 120 V ) =
|  | TOTAL CONNECTED NEUTRAL LOAD |  |  | 9000 | [12 empty] | 20 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA | ( X A X 120 V ) =
[18 empty] | 21 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA
|  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) = |  |  | 3000 | [12 empty] | 22 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | DRYERS | 1 | [6 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA
|  | 3,000-120,000 VA @ 35% ( 6,000 VA X 0.35 ) = |  |  | 2100 | [12 empty] | 23 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | SIZE | 5.5 | [6 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA
|  | OVER 120,000 VA @ 25% ( 0 VA X 0.25 ) = |  |  | 0 | [12 empty] | 24 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PHASE | 1 | [6 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA
APPLIANCES FASTENED IN PLACE NEC SECTION 220.53 |  | SUBTOTAL |  |  | 5100 | [12 empty] | 25 | PUMP | 1 | X | 16 | A X | 240 | V ) = | PUMP ( 1 X 16 A X 240 V ) = |  | 3840 | [7 empty] | CEILING | 2 |  |  |  | 5500
WATER HEATER ( 1 X 4,500 VA ) = | 4500 | [6 empty] | FIRST 200 A @ 100% ( | 61 | A X 1.00 ) = | [7 empty] | 26 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) =
FURNACE ( 1 X 7.2 A X 120 V ) = | 864 | RANGE DEMAND | [5 empty] | FIRST 200 A @ 100% ( | 61 | A X 1.00 ) = | FIRST 200 A @ 100% (61 A X 1.00 ) = | [6 empty] | 27 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | DRYER ( | 1 | DRYER X | 5500 | VA ) = | 5500
DISPOSAL ( 1 X 6.5 A X 120 V ) = | 780 | TABLE 220.55 COLUMN C | [15 empty] | 28 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | DRYER ( | 1 | DRYER X | 5,500 | VA ) = |  | DRYER ( 1 DRYER X 5,500 VA ) =
DISHWASHER ( 1 X 11.2 A X 120 V ) = | 1344 | 70% OF TABLE 220.55 ( 8,000 VA X 0.70 ) = |  |  | 5600 |  |  | REMAINDER @ 70% ( | 0 | A X 0.70 ) = | [7 empty] | 29 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) =
MIRCOWAVE ( 1 X 9.0 A X 120 V ) = | 1080 | [6 empty] | REMAINDER @ 70% ( | 0 | A X 0.70 ) = | REMAINDER @ 70% ( 0 A X 0.70 ) = | [6 empty] | 30 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | PER PHASE DEMAND ( | 5500 | VA ÷ 2 ) = | 2750 | VA
CENTRAL VAC ( 1 X 12.0 A X 120 V ) = | 1440 | DRYER DEMAND | [15 empty] | 31 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | PER PHASE DEMAND ( | 5,500 | VA ÷ 2 ) = | 2,750 | VA
|  | TABLE 220.54 | [15 empty] | 32 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) =
|  | 70% OF TABLE 220.54 ( 5,500 VA 1.00 VA X 0.70 ) = |  |  | 3850 | [12 empty] | 33 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 2750 | VA X 3 ) =
[18 empty] | 34 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 2,750 | VA X 3 ) =
|  | UNBALANCED MISC LOADS |  |  | 0
|  | NEUTRAL LOAD VA |  |  | 14550
MISC LOADS NEC 220.82(B)(4)
|  | NEUTRAL LOAD ( 14,550 VA ÷ 240 V ) = |  |  | 61
[14 empty] | WIRE CODE | #1
|  | FURTHER DEMAND FACTOR - NEC 220.61(B)(2) | [11 empty] | SER | ERROR
|  | FIRST 200 A @ 100% (61 A X 1.00 ) = |  |  | 61 |  | FEEDER TYPE | CONDUIT
|  | REMAINDER @ 70% ( 0 A X 0.70 ) = |  |  | 0 |  |  | -- | [6 empty] | #1 |  |  |  | WIRE | WIRE | SYSTEM
[19 empty] | SIZE | SIZE | GROUND
|  | MINIMUM NEUTRAL CONDUCTOR AMPACITY |  |  | 61 |  | SIZE | 3" | [6 empty] | 5 |  |  |  | AWG | CODE
[7 empty] | CONDUIT | PVC |  | 3" PVC -- |  |  |  |  | --------------------------- |  |  | 1 | #6 | 5 | #8
[7 empty] | DISPLAY | 99 |  | -- 3" PVC |  |  |  |  | #6 |  |  | 2 | #4 | 6 | #8
|  | VOLTAGE DROP CALCULATIONS | [15 empty] | 3 | #3 | 6 | #8
|  | ( 2 X 10' L X 0.2530 R X 109.0 A ÷ 1,000 ) = 0.6 VD | [5 empty] | UNDERGROUND | [6 empty] | UFER GND |  |  | 4 | #2 | 8 | #8
|  | ( 0.6 VD ÷ 240 V X 100 ) = 0.3 % VD |  |  |  |  | 60A-2P | METER | [9 empty] | 5 | #1 | 9 | #6
[8 empty] | MAIN PANEL | [6 empty] | --------------------------- #6 UFER GND |  |  | 6 | #1/0 | 10 | #6
|  | FAULT CURRENT CALCULATIONS | [15 empty] | 7 | #2/0 | 11 | #6
|  | (( 22,000 AFC X 1.00 UA ) + 0 MC ) = 22,000 AFC |  |  |  |  | FEEDER | [10 empty] | 8 | #3/0 | 12 | #4
|  | ( 2 X 10 L X 22,000 AFC ) ÷ ( 4,645 C X 1 N X 240 V ) = 0.395 CF |  |  |  | --- | 25' |  | --- 25' | [8 empty] | 9 | #3/0 | 12 | #4
|  | ( 1 ) ÷ ( 1 + 0.395 CF ) = 0.717 CM |  |  |  | --- | 1- SER CABLE |  | --- 1- SER CABLE |  | 1- SER CABLE --- | [6 empty] | 10 | #4/0 | 12 | #4
|  | ( 22,000 AFC X 0.717 CM ) = 15,774 CLC |  |  |  |  | 3-#4 AL |  | 3-#4 AL | [8 empty] | 11 | #250 | 12 | #4
[7 empty] | 1-#6 GND |  | 1-#6 GND | [8 empty] | 12 | #300 | 12 | #4
[18 empty] | 13 | #350 | 12 | #4
|  |  | KEY | [14 empty] | 14 | #400 | 12 | #4
|  |  | A - Amps | [14 empty] | 15 | #500 | 12 | #4
|  |  | AFC - Available Fault Current | [14 empty] | 16 | #600 | 12 | #4
|  |  | C - Conductor Constance | [14 empty] | 17 | #750 | 12 | #4
PUMP ( 1 X 16 A X 240 V ) = | 3840 |  | CF - Conductor Factor |  |  |  | 60A-2P | [10 empty] | 18 | #1000 | 12 | #4
CLC - Conductor Let Through Current
CM - Conductor Multiplier
|  |  | L - Length |  |  |  | SP1
MC - Motor Contribution
N - Number of Conductors
R - Resistance
UA - Utility Adjustment
V - Volts
VA - Volt Amps
VD - Voltage Drop
TOTAL GENERAL LOAD | 40348
FIRST 10 KVA AT 100% | 10000
REMAINDER OF LOAD AT 40% | 12139.2
SUB TOTAL GENERAL LOAD | 22139.2
LARGEST HEATING OR COOLING LOAD | 4000
TOTAL KVA | 26139.2
TOTAL AMPS ( 26,139 VA ÷ 240 V ) = | 109 |  | Prepared With Service Pro 2026 Software | [21 empty] | TEXT
FUTURE AMPS ( 0% ) | 0 |  | Copyright Durand & Associates | [15 empty] | (1) AC LOAD ( |  |  |  | VA | 4000 | 4,000 | VA X 100% ) = | (1) AC LOAD ( 4,000 VA X 100% ) = 4,000 VA | 4000
DESIGN AMPS | 109 |  | www.durandassociates.com | [15 empty] | (2) HEAT PUMPS NO SUPP ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (2) HEAT PUMPS NO SUPP ( 0 VA X 100% ) = 0 VA | 0
[19 empty] | (3) HEAT PUMPS ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (3) HEAT PUMPS ( 0 VA X 100% ) = 0 VA | 0 |  |  | SUPPLEMENTAL HEAT ( | 0 | 0 | VA X 65% ) = | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = |  |  |  | 0 | 0 | VA | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = 0 VA
[19 empty] | (4) ELECTRIC SPACE ( |  |  |  | VA | 0 | 0 | VA X 65% ) = | (4) ELECTRIC SPACE ( 0 VA X 65% ) = 0 VA | 0 | 0 |  | (4) ELECTRIC SPACE ( 0 VA X 65% ) = 0 VA
[19 empty] | (5) SPACE HEATING ( |  |  |  | VA | 0 | 0 | VA X 40% ) = | (5) SPACE HEATING ( 0 VA X 40% ) = 0 VA | 0 | 0
[19 empty] | (6) SPACE HEATING ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (6) SPACE HEATING (0 VA X 100% ) = 0 VA | 0 | 0 |  | SUPPLEMENTAL HEAT ( | 0 | 0 | VA X 65% ) = | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = |  |  |  | 0 | 0 | VA | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = 0 VA
4000
[19 empty] | 26139.2 |  |  |  |  | 26,139 | VA ÷ | 240 | V ) = | 109 |  |  | =
[33 empty] | 1 | 4000 |  | 4000 | 4000 | 1 | 4000
[24 empty] | TOTAL AMPS ( |  |  | TOTAL AMPS ( 26,139 VA ÷ 240 V ) = | [5 empty] | 2 | 0 |  | 0 | 0 | 0 | 0
[19 empty] | NEUTRAL | [13 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | FIRST 3,000 VA @ 100% ( | 3000 |  | 3,000 | VA X 1.00 ) = |  |  |  |  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) = | [5 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0
[33 empty] | 5 | 0 |  | 0 | 0 | 0 | 0
[18 empty] | 3,000-120,000 VA @ 35% ( | 9000 |  | 3000 | 6000 | 6,000 | VA X 0.35 ) = |  |  | 3,000-120,000 VA @ 35% ( 6,000 VA X 0.35 ) = | 2100 |  |  |  |  | 6 | 0 |  | 0 | 0 | 0 | 0
[18 empty] | OVER 120,000 VA @ 25% ( | 0 |  |  | 0 |  | VA X 0.25 ) = |  |  | OVER 120,000 VA @ 25% ( 0 VA X 0.25 ) = | 0 | [10 empty] | 4000
RANGE
[16 empty] | 70% OF TABLE |  | 70% OF TABLE 220.55 ( | 8000 |  |  | 8,000 |  | VA X 0.70 ) = |  |  | 70% OF TABLE 220.55 ( 8,000 VA X 0.70 ) = | 5600
[16 empty] | 70% OF TABLE |  |  | DRYER |  |  |  | 1
[18 empty] | 70% OF TABLE 220.54 ( | 5500 |  |  | 5,500 | 1.00 | VA X 0.70 ) = | VA |  | 70% OF TABLE 220.54 ( 5,500 VA 1.00 VA X 0.70 ) = | 3850 | 3850 | 2695
UNBALANCED
[19 empty] | 0 |  |  | 0 |  | VA X 1.00 = |  |  | 0 VA X 1.00 = | 0
NEUTRAL AMPS
[18 empty] | NEUTRAL LOAD ( | 14550 |  |  | 14,550 |  | VA ÷ | 240 | V ) = | NEUTRAL LOAD ( 14,550 VA ÷ 240 V ) = |  | 61
[7 empty] | >> |  | 1
[8 empty] | VD | 2
[8 empty] | AFC | 3 | [9 empty] | FUTUR AMPS (
[9 empty] | 4 | [9 empty] | 109 |  |  | 109 |  | A X | 0 | = | 109 A X 0 =
[22 empty] | FUTURE AMPS |  | ( | 0 | % ) | FUTURE AMPS ( 0% )
[9 empty] | 4 |  | 1 |  | 2 |  | 3 |  | 4
[9 empty] | A - Amps |  | A - Amps |  | A - Amps |  | A - Amps |  | A - Amps
[9 empty] | AFC - Available Fault Current |  | VA - Volt Amps |  | L - Length |  | AFC - Available Fault Current |  | AFC - Available Fault Current
[9 empty] | C - Conductor Constance |  |  |  | R - Resistance |  | C - Conductor Constance |  | C - Conductor Constance
[9 empty] | CF - Conductor Factor |  |  |  | V - Volts |  | CF - Conductor Factor |  | CF - Conductor Factor
[9 empty] | CLC - Conductor Let Through Current |  |  |  | VA - Volt Amps |  | CLC - Conductor Let Through Current |  | CLC - Conductor Let Through Current
[9 empty] | CM - Conductor Multiplier |  |  |  | VD - Voltage Drop |  | CM - Conductor Multiplier |  | CM - Conductor Multiplier
[9 empty] | L - Length | [5 empty] | L - Length |  | L - Length
[9 empty] | MC - Motor Contribution | [5 empty] | MC - Motor Contribution |  | MC - Motor Contribution
[9 empty] | N - Number of Conductors | [5 empty] | N - Number of Conductors |  | N - Number of Conductors
[9 empty] | R - Resistance | [5 empty] | UA - Utility Adjustment |  | R - Resistance
[9 empty] | UA - Utility Adjustment | [5 empty] | V - Volts |  | UA - Utility Adjustment
[9 empty] | V - Volts | [5 empty] | VA - Volt Amps |  | V - Volts
[9 empty] | VA - Volt Amps | [7 empty] | VA - Volt Amps
[9 empty] | VD - Voltage Drop | [7 empty] | VD - Voltage Drop
0

## Dir Input
NUMBER OF CIRCUITS IN PANEL |  | 42
CIRCUIT DIRECTORY PANEL |  |  |  |  | 0
CIR | DESCRIPTION | DESCRIPTION | CIR
1 | MICROWAVE | RANGE | 2 | 2 | 1
3 | DISPOSAL | RANGE | 4 | 4 | 1
5 | FURNACE |  | 6 | 6 | 1
7 |  |  | 8 | 8 | 1
9 |  |  | 10 | 10 | 1
11 |  |  | 12 | 12 | 1
13 |  |  | 14 | 14 | 1
15 |  |  | 16 | 16 | 1
17 |  |  | 18 | 18 | 1
19 |  |  | 20 | 20 | 1
21 |  |  | 22 | 22 | 1
23 |  |  | 24 | 24 | 1
25 |  |  | 26 | 26 | 1
27 |  |  | 28 | 28 | 1
29 |  |  | 30 | 30 | 1
31 |  |  | 32 | 32 | 1
33 |  |  | 34 | 34 | 1
35 |  |  | 36 | 36 | 1
37 |  |  | 38 | 38 | 1
39 |  |  | 40 | 40 | 1
41 |  |  | 42 | 42 | 1

## Dir Print
CIRCUIT DIRECTORY PANEL | [5 empty] | 0
CIR | DESCRIPTION | DESCRIPTION | CIR
1 | MICROWAVE | RANGE | 2 | 42 | 2 | 1
3 | DISPOSAL | RANGE | 4 |  | 4 | 1
5 | FURNACE |  | 6 |  | 6 | 1
7 |  |  | 8 |  | 8 | 1
9 |  |  | 10 |  | 10 | 1
11 |  |  | 12 |  | 12 | 1
13 |  |  | 14 |  | 14 | 1
15 |  |  | 16 |  | 16 | 1
17 |  |  | 18 |  | 18 | 1
19 |  |  | 20 |  | 20 | 1
21 |  |  | 22 |  | 22 | 1
23 |  |  | 24 |  | 24 | 1
25 |  |  | 26 |  | 26 | 1
27 |  |  | 28 |  | 28 | 1
29 |  |  | 30 |  | 30 | 1
31 |  |  | 32 |  | 32 | 1
33 |  |  | 34 |  | 34 | 1
35 |  |  | 36 |  | 36 | 1
37 |  |  | 38 |  | 38 | 1
39 |  |  | 40 |  | 40 | 1
41 |  |  | 42 |  | 42 | 1

## Opt Calcs (hidden)
[9 empty] | CODE YEAR | 2008 | [10 empty] | (
SINGLE FAMILY SERVICE LOAD CALCULATIONS |  | PROJECT NAME |  | SAMPLE |  |  | 0 |  |  |  |  | TOTAL SQ FOOTAGE ( | [6 empty] | MISC LOADS
BASED ON THE 2008 NEC SECTION 220.82 |  | DWELLING UNIT |  | MAIN PANEL |  |  | 0 |  |  |  |  | APPLIANCE CIRCUITS ( | [5 empty] | 1 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | WATER HEATER | ( | 1 | X | 4500 | VA X |  |  | 1 | ) = | 4500 | VA
[12 empty] | LAUNDRY CIRCUITS ( | [5 empty] | 2 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | FURNACE | ( | 1 | X | 7.2 | X | 120 | X | 1 | ) = | 864 | VA
GENERAL LOADS NEC 220.82(B) |  | HEATING & COOLING LOADS - NEC 220.82(C) | [15 empty] | 3 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | DISPOSAL | ( | 1 | X | 6.5 | X | 120 | X | 1 | ) = | 780 | VA
TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = | 4500 | (1) AC LOAD ( 4,000 VA X 100% ) = 4,000 VA |  |  | < < LARGEST |  |  | 1,500 | SQ FT X 3 VA ) = |  |  | TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = | [5 empty] | 4 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | RANGES | 1 | [5 empty] | DISHWASHER | ( | 1 | X | 11.2 | X | 120 | X | 1 | ) = | 1344 | VA
APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = | 3000 | (2) HEAT PUMPS NO SUPP ( 0 VA X 100% ) = 0 VA | [5 empty] | 2 | X 1,500 VA ) = |  |  | APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = | [5 empty] | 5 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | SIZE | 12 | [5 empty] | MIRCOWAVE | ( | 1 | X | 9 | X | 120 | X | 1 | ) = | 1080 | VA
LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = | 1500 | (3) HEAT PUMPS ( 0 VA X 100% ) = 0 VA | [5 empty] | 1 | X 1,500 VA ) = |  |  | LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = | [5 empty] | 6 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PHASE | 1 | [5 empty] | CENTRAL VAC | ( | 1 | X | 12 | X | 120 | X | 1 | ) = | 1440 | VA
|  | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = 0 VA | [5 empty] | 1 | X | 12,000 | VA = | 1 X 12,000 VA = | [5 empty] | 7 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | CEILING | 2 | [6 empty] | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | (4) ELECTRIC SPACE ( 0 VA X 65% ) = 0 VA | [5 empty] | 1 | X | 5,500 | VA = | 1 X 5,500 VA = | [5 empty] | 8 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | LESS THAN FOUR SEPARATELY CONTROLLED UNITS. | [5 empty] | 1 | X | 4,500 | VA ) = | WATER HEATERS ( 1 X 4,500 VA ) = | [5 empty] | 9 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | RANGE ( | 1 | RANGE X | 12000 | VA ) = | 12000 |  |  | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | (5) SPACE HEATING ( 0 VA X 40% ) = 0 VA | [15 empty] | 10 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | RANGE ( | 1 | RANGE X | 12,000 | VA ) = |  | RANGE ( 1 RANGE X 12,000 VA ) = |  | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | MORE THAN FOUR SEPARATELY CONTROLLED UNITS. | [9 empty] | WATER HEATERS ( | [5 empty] | 11 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | X | 120 | X | 1 | ) = |  | VA
|  | (6) SPACE HEATING (0 VA X 100% ) = 0 VA | [15 empty] | 12 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PER PHASE DEMAND ( | 12000 | VA ÷ 2 ) = | 6000 | VA |  |  |  |  | 1
RANGE ( 1 RANGE X 12,000 VA ) = | 12000 | CONTINUOUS AT THE FULL NAMEPLATE VALUE. | [15 empty] | 13 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PER PHASE DEMAND ( | 12,000 | VA ÷ 2 ) = | 6,000 | VA
|  | LARGEST HEATING OR COOLING LOAD |  |  | 4000 | [12 empty] | 14 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | WATER HEATER | ( | 1 | X | 4,500 | VA |  |  |  | ) = | 4,500 | VA | WATER HEATER ( 1 X 4,500 VA ) =
[8 empty] | MISC LOADS | 3840 | [8 empty] | 15 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 6000 | VA X 3 ) = |  |  |  |  | FURNACE | ( | 1 | X | 7.2 | A X | 120 | V |  | ) = | 864 | VA | FURNACE ( 1 X 7.2 A X 120 V ) =
|  | NEUTRAL LOAD NEC 220.61 | [15 empty] | 16 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 6,000 | VA X 3 ) = |  |  |  |  | DISPOSAL | ( | 1 | X | 6.5 | A X | 120 | V |  | ) = | 780 | VA | DISPOSAL ( 1 X 6.5 A X 120 V ) =
|  | TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = |  |  | 4500 | [12 empty] | 17 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | DISHWASHER | ( | 1 | X | 11.2 | A X | 120 | V |  | ) = | 1,344 | VA | DISHWASHER ( 1 X 11.2 A X 120 V ) =
|  | APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = |  |  | 3000 | [12 empty] | 18 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | MIRCOWAVE | ( | 1 | X | 9.0 | A X | 120 | V |  | ) = | 1,080 | VA | MIRCOWAVE ( 1 X 9.0 A X 120 V ) =
DRYER ( 1 DRYER X 5,500 VA ) = | 5500 | LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = |  |  | 1500 | [12 empty] | 19 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | CENTRAL VAC | ( | 1 | X | 12.0 | A X | 120 | V |  | ) = | 1,440 | VA | CENTRAL VAC ( 1 X 12.0 A X 120 V ) =
|  | TOTAL CONNECTED NEUTRAL LOAD |  |  | 9000 | [12 empty] | 20 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA
[18 empty] | 21 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA
|  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) = |  |  | 3000 | [12 empty] | 22 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | DRYERS | 1 | [6 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA
|  | 3,000-120,000 VA @ 35% ( 6,000 VA X 0.35 ) = |  |  | 2100 | [12 empty] | 23 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | SIZE | 5.5 | [6 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA
|  | OVER 120,000 VA @ 25% ( 0 VA X 0.25 ) = |  |  | 0 | [12 empty] | 24 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PHASE | 1 | [6 empty] | ( |  | X |  | A X | 120 | V |  | ) = |  | VA
APPLIANCES FASTENED IN PLACE NEC SECTION 220.53 |  | SUBTOTAL |  |  | 5100 | [12 empty] | 25 | PUMP | 1 | X | 16 | A X | 240 | V ) = | PUMP ( 1 X 16 A X 240 V ) = |  | 3840 | [7 empty] | CEILING | 2 |  |  |  | 5500
WATER HEATER ( 1 X 4,500 VA ) = | 4500 | [6 empty] | FIRST 200 A @ 100% ( | 61 | A X 1.00 ) = | [7 empty] | 26 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) =
FURNACE ( 1 X 7.2 A X 120 V ) = | 864 | RANGE DEMAND | [5 empty] | FIRST 200 A @ 100% ( | 61 | A X 1.00 ) = | FIRST 200 A @ 100% (61 A X 1.00 ) = | [6 empty] | 27 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | DRYER ( | 1 | DRYER X | 5500 | VA ) = | 5500
DISPOSAL ( 1 X 6.5 A X 120 V ) = | 780 | TABLE 220.55 COLUMN C | [15 empty] | 28 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | DRYER ( | 1 | DRYER X | 5,500 | VA ) = |  | DRYER ( 1 DRYER X 5,500 VA ) =
DISHWASHER ( 1 X 11.2 A X 120 V ) = | 1344 | 70% OF TABLE 220.55 ( 8,000 VA X 0.70 ) = |  |  | 5600 |  |  | REMAINDER @ 70% ( | 0 | A X 0.70 ) = | [7 empty] | 29 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) =
MIRCOWAVE ( 1 X 9.0 A X 120 V ) = | 1080 | [6 empty] | REMAINDER @ 70% ( | 0 | A X 0.70 ) = | REMAINDER @ 70% ( 0 A X 0.70 ) = | [6 empty] | 30 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | PER PHASE DEMAND ( | 5500 | VA ÷ 2 ) = | 2750 | VA
CENTRAL VAC ( 1 X 12.0 A X 120 V ) = | 1440 | DRYER DEMAND | [15 empty] | 31 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | PER PHASE DEMAND ( | 5,500 | VA ÷ 2 ) = | 2,750 | VA
|  | TABLE 220.54 | [15 empty] | 32 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) =
|  | 70% OF TABLE 220.54 ( 5,500 VA 1.00 VA X 0.70 ) = |  |  | 3850 |  | UNDERGROUND | [10 empty] | 33 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 2750 | VA X 3 ) =
[7 empty] | METER | [10 empty] | 34 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 2,750 | VA X 3 ) =
|  | UNBALANCED MISC LOADS |  |  | 0
0
|  | NEUTRAL LOAD VA |  |  | 14550
MISC LOADS NEC 220.82(B)(4)
|  | NEUTRAL LOAD ( 14,550 VA ÷ 240 V ) = |  |  | 61
[14 empty] | WIRE CODE | #1
|  | FURTHER DEMAND FACTOR - NEC 220.61(B)(2) | [11 empty] | SER | ERROR | [5 empty] | AL
|  | FIRST 200 A @ 100% (61 A X 1.00 ) = |  |  | 61 |  | FEEDER TYPE | CONDUIT
|  | REMAINDER @ 70% ( 0 A X 0.70 ) = |  |  | 0 |  |  | -- | [6 empty] | #1 |  |  |  | WIRE | WIRE | SYSTEM | SYSTEM | SYSTEM
[19 empty] | SIZE | SIZE | GROUND | GROUND | GROUND
|  | MINIMUM NEUTRAL CONDUCTOR AMPACITY |  |  | 61 |  | SIZE | 3" | [6 empty] | 5 |  |  |  | AWG | CODE |  | CU | AL
[7 empty] | CONDUIT | PVC |  | 3" PVC -- |  |  |  |  | --------------------------- |  |  | 1 | #6 | 5 | #8 | #8 | #8
[7 empty] | DISPLAY | 99 |  | -- 3" PVC |  |  |  |  | #8 | CU | #8 CU | 2 | #4 | 6 | #8 | #8 | #8
|  | VOLTAGE DROP CALCULATIONS | [15 empty] | 3 | #3 | 6 | #8 | #8 | #8
|  | ( 2 X 10' L X 0.2530 R X 109.0 A ÷ 1,000 ) = 0.6 VD | [5 empty] | UNDERGROUND | [6 empty] | UFER GND |  |  | 4 | #2 | 8 | #8 | #8 | #8
|  | ( 0.6 VD ÷ 240 V X 100 ) = 0.3 % VD |  |  |  |  | 60A-2P | METER | [9 empty] | 5 | #1 | 9 | #8 | #6 | #8
[8 empty] | MAIN PANEL | [6 empty] | --------------------------- #8 UFER GND |  |  | 6 | #1/0 | 10 | #8 | #6 | #8
|  | FAULT CURRENT CALCULATIONS | [15 empty] | 7 | #2/0 | 11 | #6 | #6 | #6
|  | (( 22,000 AFC X 1.00 UA ) + 0 MC ) = 22,000 AFC |  |  |  |  | FEEDER | [10 empty] | 8 | #3/0 | 12 | #6 | #4 | #6
|  | ( 2 X 10 L X 22,000 AFC ) ÷ ( 4,645 C X 1 N X 240 V ) = 0.395 CF |  |  |  | --- | 25' |  | --- 25' | [8 empty] | 9 | #3/0 | 12 | #4 | #4 | #4
|  | ( 1 ) ÷ ( 1 + 0.395 CF ) = 0.717 CM |  |  |  | --- | 1- SER CABLE |  | --- 1- SER CABLE |  | 1- SER CABLE --- | [6 empty] | 10 | #4/0 | 12 | #4 | #4 | #4
|  | ( 22,000 AFC X 0.717 CM ) = 15,774 CLC |  |  |  |  | 3-#4 AL |  | 3-#4 AL | [8 empty] | 11 | #250 | 12 | #4 | #4 | #4
[7 empty] | 1-#6 GND |  | 1-#6 GND | [8 empty] | 12 | #300 | 12 | #4 | #4 | #4
[18 empty] | 13 | #350 | 12 | #4 | #4 | #4
|  |  | KEY | [14 empty] | 14 | #400 | 12 | #4 | #4 | #4
|  |  | A - Amps | [14 empty] | 15 | #500 | 12 | #4 | #4 | #4
|  |  | AFC - Available Fault Current | [14 empty] | 16 | #600 | 12 | #4 | #4 | #4
|  |  | C - Conductor Constance | [14 empty] | 17 | #750 | 12 | #4 | #4 | #4
PUMP ( 1 X 16 A X 240 V ) = | 3840 |  | CF - Conductor Factor |  |  |  | 60A-2P | [10 empty] | 18 | #1000 | 12 | #4 | #4 | #4
CLC - Conductor Let Through Current
CM - Conductor Multiplier
|  |  | L - Length |  |  |  | SP1
MC - Motor Contribution
N - Number of Conductors
R - Resistance
UA - Utility Adjustment
V - Volts
VA - Volt Amps
VD - Voltage Drop
TOTAL GENERAL LOAD | 40348
FIRST 10 KVA AT 100% | 10000
REMAINDER OF LOAD AT 40% | 12139.2
SUB TOTAL GENERAL LOAD | 22139.2
LARGEST HEATING OR COOLING LOAD | 4000
TOTAL KVA | 26139.2
TOTAL AMPS ( 26,139 VA ÷ 240 V ) = | 109 | [23 empty] | TEXT
FUTURE AMPS ( 0% ) | 0 |  | Prepared With Service Pro 2008 Software | [15 empty] | (1) AC LOAD ( |  |  |  | VA | 4000 | 4,000 | VA X 100% ) = | (1) AC LOAD ( 4,000 VA X 100% ) = 4,000 VA | 4000
DESIGN AMPS | 109 |  | Copyright Durand & Associates | [15 empty] | (2) HEAT PUMPS NO SUPP ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (2) HEAT PUMPS NO SUPP ( 0 VA X 100% ) = 0 VA | 0
[19 empty] | (3) HEAT PUMPS ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (3) HEAT PUMPS ( 0 VA X 100% ) = 0 VA | 0 |  |  | SUPPLEMENTAL HEAT ( | 0 | 0 | VA X 65% ) = | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = |  |  |  | 0 | 0 | VA | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = 0 VA
[19 empty] | (4) ELECTRIC SPACE ( |  |  |  | VA | 0 | 0 | VA X 65% ) = | (4) ELECTRIC SPACE ( 0 VA X 65% ) = 0 VA | 0 | 0 |  | (4) ELECTRIC SPACE ( 0 VA X 65% ) = 0 VA
[19 empty] | (5) SPACE HEATING ( |  |  |  | VA | 0 | 0 | VA X 40% ) = | (5) SPACE HEATING ( 0 VA X 40% ) = 0 VA | 0 | 0
[19 empty] | (6) SPACE HEATING ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (6) SPACE HEATING (0 VA X 100% ) = 0 VA | 0 | 0 |  | SUPPLEMENTAL HEAT ( | 0 | 0 | VA X 65% ) = | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = |  |  |  | 0 | 0 | VA | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = 0 VA
4000
[19 empty] | 26139.2 |  |  |  |  | 26,139 | VA ÷ | 240 | V ) = | 109 |  |  | =
[33 empty] | 1 | 4000 |  | 4000 | 4000 | 1 | 4000
[24 empty] | TOTAL AMPS ( |  |  | TOTAL AMPS ( 26,139 VA ÷ 240 V ) = | [5 empty] | 2 | 0 |  | 0 | 0 | 0 | 0
[19 empty] | NEUTRAL | [13 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | FIRST 3,000 VA @ 100% ( | 3000 |  | 3,000 | VA X 1.00 ) = |  |  |  |  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) = | [5 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0
[33 empty] | 5 | 0 |  | 0 | 0 | 0 | 0
[18 empty] | 3,000-120,000 VA @ 35% ( | 9000 |  | 3000 | 6000 | 6,000 | VA X 0.35 ) = |  |  | 3,000-120,000 VA @ 35% ( 6,000 VA X 0.35 ) = | 2100 |  |  |  |  | 6 | 0 |  | 0 | 0 | 0 | 0
[18 empty] | OVER 120,000 VA @ 25% ( | 0 |  |  | 0 |  | VA X 0.25 ) = |  |  | OVER 120,000 VA @ 25% ( 0 VA X 0.25 ) = | 0 | [10 empty] | 4000
RANGE
[16 empty] | 70% OF TABLE |  | 70% OF TABLE 220.55 ( | 8000 |  |  | 8,000 |  | VA X 0.70 ) = |  |  | 70% OF TABLE 220.55 ( 8,000 VA X 0.70 ) = | 5600
[16 empty] | 70% OF TABLE |  |  | DRYER |  |  |  | 1
[18 empty] | 70% OF TABLE 220.54 ( | 5500 |  |  | 5,500 | 1.00 | VA X 0.70 ) = | VA |  | 70% OF TABLE 220.54 ( 5,500 VA 1.00 VA X 0.70 ) = | 3850 | 3850 | 2695
UNBALANCED
[19 empty] | 0 |  |  | 0 |  | VA X 1.00 = |  |  | 0 VA X 1.00 = | 0
[11 empty] | UNDERGROUND | [7 empty] | NEUTRAL AMPS
[11 empty] | METER | [6 empty] | NEUTRAL LOAD ( | 14550 |  |  | 14,550 |  | VA ÷ | 240 | V ) = | NEUTRAL LOAD ( 14,550 VA ÷ 240 V ) = |  | 61
[7 empty] | >> |  | 1 |  | 0
[8 empty] | VD | 2
[8 empty] | AFC | 3 | [9 empty] | FUTUR AMPS (
[9 empty] | 4 | [9 empty] | 109 |  |  | 109 |  | A X | 0 | = | 109 A X 0 =
[22 empty] | FUTURE AMPS |  | ( | 0 | % ) | FUTURE AMPS ( 0% )
[9 empty] | 4 |  | 1 |  | 2 |  | 3 |  | 4 |  | 5
[9 empty] | A - Amps |  | A - Amps |  | A - Amps |  | A - Amps |  | A - Amps |  | A - Amps
[9 empty] | AFC - Available Fault Current |  | V - Volts |  | L - Length |  | AFC - Available Fault Current |  | AFC - Available Fault Current |  | AFC - Available Fault Current
[9 empty] | C - Conductor Constance |  | VA - Volt Amps |  | R - Resistance |  | C - Conductor Constance |  | C - Conductor Constance |  | MC - Motor Contribution
[9 empty] | CF - Conductor Factor |  |  |  | V - Volts |  | CF - Conductor Factor |  | CF - Conductor Factor |  | UA - Utility Adjustment
[9 empty] | CLC - Conductor Let Through Current |  |  |  | VA - Volt Amps |  | CLC - Conductor Let Through Current |  | CLC - Conductor Let Through Current |  | V - Volts
[9 empty] | CM - Conductor Multiplier |  |  |  | VD - Voltage Drop |  | CM - Conductor Multiplier |  | CM - Conductor Multiplier |  | VA - Volt Amps
[9 empty] | L - Length | [5 empty] | L - Length |  | L - Length
[9 empty] | MC - Motor Contribution | [5 empty] | MC - Motor Contribution |  | MC - Motor Contribution
[9 empty] | N - Number of Conductors | [5 empty] | N - Number of Conductors |  | N - Number of Conductors
[9 empty] | R - Resistance | [5 empty] | UA - Utility Adjustment |  | R - Resistance
[9 empty] | UA - Utility Adjustment | [5 empty] | V - Volts |  | UA - Utility Adjustment
[9 empty] | V - Volts | [5 empty] | VA - Volt Amps |  | V - Volts
[9 empty] | VA - Volt Amps | [7 empty] | VA - Volt Amps
[9 empty] | VD - Voltage Drop | [7 empty] | VD - Voltage Drop

## Std Calcs (hidden)
[10 empty] | CODE YEAR | 2008 | [10 empty] | (
SINGLE FAMILY SERVICE LOAD CALCULATIONS |  |  | PROJECT NAME |  | SAMPLE |  |  | 0 |  |  |  |  | TOTAL SQ FOOTAGE ( | [6 empty] | MISC LOADS
BASED ON THE 2008 NEC SECTION 220.40 |  |  | DWELLING UNIT |  | MAIN PANEL |  |  | 0 |  |  |  |  | APPLIANCE CIRCUITS ( | [5 empty] | 1 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | WATER HEATER | ( | 1 | X | 4500 | VA X |  |  | 0.75 | ) = | 3375 | VA
[13 empty] | LAUNDRY CIRCUITS ( | [5 empty] | 2 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | FURNACE | ( | 1 | X | 7 | X | 120 | X | 0.75 | ) = | 630 | VA
GENERAL LOADS NEC 220.42 |  |  | HEATING & COOLING LOADS - NEC 220.82(C) | [15 empty] | 3 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | DISPOSAL | ( | 1 | X | 7 | X | 120 | X | 0.75 | ) = | 630 | VA
TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = |  | 4500 | (1) AC LOAD ( 4,000 VA X 100% ) = 4,000 VA |  |  | < < LARGEST |  |  | 1,500 | SQ FT X 3 VA ) = |  |  | TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = | [5 empty] | 4 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | RANGES | 1 | [5 empty] | DISHWASHER | ( | 1 | X | 11 | X | 120 | X | 0.75 | ) = | 990 | VA
APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = |  | 3000 | (2) HEAT PUMPS NO SUPP ( 0 VA X 100% ) = 0 VA | [5 empty] | 2 | X 1,500 VA ) = |  |  | APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = | [5 empty] | 5 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | SIZE | 12 | [5 empty] | MIRCOWAVE | ( | 1 | X | 9 | X | 120 | X | 0.75 | ) = | 810 | VA
LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = |  | 1500 | (3) HEAT PUMPS ( 0 VA X 100% ) = 0 VA | [5 empty] | 1 | X 1,500 VA ) = |  |  | LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = | [5 empty] | 6 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PHASE | 1 | [5 empty] | CENTRAL VAC | ( | 1 | X | 12 | X | 120 | X | 0.75 | ) = | 1080 | VA
| TOTAL | 9000 | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = 0 VA | [5 empty] | 1 | X | 12,000 | VA = | 1 X 12,000 VA = | [5 empty] | 7 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | CEILING | 2 | [6 empty] | ( |  | X |  | X | 120 | X | 0.75 | ) = |  | VA
|  |  | (4) ELECTRIC SPACE ( 0 VA X 65% ) = 0 VA | [5 empty] | 1 | X | 5,500 | VA = | 1 X 5,500 VA = | [5 empty] | 8 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | X | 120 | X | 0.75 | ) = |  | VA
FIRST 3,000 VA AT 100% |  | 3000 | LESS THAN FOUR SEPARATELY CONTROLLED UNITS. | [5 empty] | 1 | X | 4,500 | VA ) = | WATER HEATERS ( 1 X 4,500 VA ) = | [5 empty] | 9 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | RANGE ( | 1 | RANGE X | 8000 | VA ) = | 8000 |  |  | ( |  | X |  | X | 120 | X | 0.75 | ) = |  | VA
REMAINING VA AT 35% |  | 2100 | (5) SPACE HEATING ( 0 VA X 40% ) = 0 VA | [15 empty] | 10 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | RANGE ( | 1 | RANGE X | 8,000 | VA ) = |  |  |  | ( |  | X |  | X | 120 | X | 0.75 | ) = |  | VA
| NET LOAD | 5100 | MORE THAN FOUR SEPARATELY CONTROLLED UNITS. | [9 empty] | WATER HEATERS ( | [5 empty] | 11 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | X | 120 | X | 0.75 | ) = |  | VA
|  |  | (6) SPACE HEATING (0 VA X 100% ) = 0 VA | [15 empty] | 12 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PER PHASE DEMAND ( | 8000 | VA ÷ 2 ) = | 4000 | VA |  |  |  |  | 6
RANGE ( 1 AT 12,000 VA ) |  |  | CONTINUOUS AT THE FULL NAMEPLATE VALUE. | [15 empty] | 13 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PER PHASE DEMAND ( | 8,000 | VA ÷ 2 ) = | 4,000 | VA
PER TABLE 220.55 ( 8,000 VA X 1.00 ) = VA |  | 8000 | LARGEST HEATING OR COOLING LOAD |  |  | 4000 | [12 empty] | 14 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | WATER HEATER | ( | 1 | X | 4,500 | VA X |  |  | 0.75 | ) = | 3,375 | VA | WATER HEATER ( 1 X 4,500 VA X 0.75 ) =
[9 empty] | MISC LOADS | 7840 | [8 empty] | 15 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 4000 | VA X 3 ) = |  |  |  |  | FURNACE | ( | 1 | X | 7 | A X | 120 | V X | 0.75 | ) = | 630 | VA | FURNACE ( 1 X 7 A X 120 V X 0.75 ) =
|  |  | NEUTRAL LOAD NEC 220.61 | [15 empty] | 16 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 4,000 | VA X 3 ) = |  |  |  |  | DISPOSAL | ( | 1 | X | 7 | A X | 120 | V X | 0.75 | ) = | 630 | VA | DISPOSAL ( 1 X 7 A X 120 V X 0.75 ) =
|  |  | TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = |  |  | 4500 | [12 empty] | 17 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | DISHWASHER | ( | 1 | X | 11 | A X | 120 | V X | 0.75 | ) = | 990 | VA | DISHWASHER ( 1 X 11 A X 120 V X 0.75 ) =
|  |  | APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = |  |  | 3000 | [12 empty] | 18 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | MIRCOWAVE | ( | 1 | X | 9 | A X | 120 | V X | 0.75 | ) = | 810 | VA | MIRCOWAVE ( 1 X 9 A X 120 V X 0.75 ) =
DRYER ( 1 AT 5,500 VA ) |  |  | LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = |  |  | 1500 | [12 empty] | 19 |  | 0 | X | 0 | A X | 120 | V ) = | [17 empty] | CENTRAL VAC | ( | 1 | X | 12 | A X | 120 | V X | 0.75 | ) = | 1,080 | VA | CENTRAL VAC ( 1 X 12 A X 120 V X 0.75 ) =
PER TABLE 220.54 ( 1 X 5,500 X 1.00 ) = |  | 5500 | TOTAL CONNECTED NEUTRAL LOAD |  |  | 9000 | [12 empty] | 20 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | A X | 120 | V X | 0.75 | ) = |  | VA
[19 empty] | 21 |  | 0 | X | 0 | A X | 120 | V ) = | [18 empty] | ( |  | X |  | A X | 120 | V X | 0.75 | ) = |  | VA
|  |  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) = |  |  | 3000 | [12 empty] | 22 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | DRYERS | 1 | [6 empty] | ( |  | X |  | A X | 120 | V X | 0.75 | ) = |  | VA
|  |  | 3,000-120,000 VA @ 35% ( 6,000 VA X 0.35 ) = |  |  | 2100 | [12 empty] | 23 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | SIZE | 5.5 | [6 empty] | ( |  | X |  | A X | 120 | V X | 0.75 | ) = |  | VA
|  |  | OVER 120,000 VA @ 25% ( 0 VA X 0.25 ) = |  |  | 0 | [12 empty] | 24 |  | 0 | X | 0 | A X | 120 | V ) = | [10 empty] | PHASE | 1 | [6 empty] | ( |  | X |  | A X | 120 | V X | 0.75 | ) = |  | VA
APPLIANCES FASTENED IN PLACE NEC SECTION 220.53 |  |  | SUBTOTAL |  |  | 5100 | [12 empty] | 25 | PUMP | 1 | X | 16 | A X | 240 | V ) = | PUMP ( 1 X 16 A X 240 V ) = |  | 3840 | [7 empty] | CEILING | 2 |  |  |  | 5500
WATER HEATER ( 1 X 4,500 VA X 0.75 ) = |  | 3375 | [6 empty] | FIRST 200 A @ 100% ( | 61 | A X 1.00 ) = | [7 empty] | 26 |  | 0 | X | 0 | A X | 240 | V ) =
FURNACE ( 1 X 7 A X 120 V X 0.75 ) = |  | 630 | RANGE DEMAND | [5 empty] | FIRST 200 A @ 100% ( | 61 | A X 1.00 ) = | FIRST 200 A @ 100% (61 A X 1.00 ) = | [6 empty] | 27 |  | 0 | X | 0 | A X | 240 | V ) = | [10 empty] | DRYER ( | 1 | RANGE X | 5500 | VA ) = | 5500
DISPOSAL ( 1 X 7 A X 120 V X 0.75 ) = |  | 630 | TABLE 220.55 COLUMN C | [15 empty] | 28 |  | 0 | X | 0 | A X | 240 | V ) = | [10 empty] | DRYER ( | 1 | RANGE X | 5,500 | VA ) =
DISHWASHER ( 1 X 11 A X 120 V X 0.75 ) = |  | 990 | 70% OF TABLE 220.55 ( 8,000 VA X 0.70 ) = |  |  | 5600 |  |  | REMAINDER @ 70% ( | 0 | A X 0.70 ) = | [7 empty] | 29 |  | 0 | X | 0 | A X | 240 | V ) =
MIRCOWAVE ( 1 X 9 A X 120 V X 0.75 ) = |  | 810 | [6 empty] | REMAINDER @ 70% ( | 0 | A X 0.70 ) = | REMAINDER @ 70% ( 0 A X 0.70 ) = | [6 empty] | 30 |  | 0 | X | 0 | A X | 240 | V ) = | [10 empty] | PER PHASE DEMAND ( | 5500 | VA ÷ 2 ) = | 2750 | VA
CENTRAL VAC ( 1 X 12 A X 120 V X 0.75 ) = |  | 1080 | DRYER DEMAND | [15 empty] | 31 |  | 0 | X | 0 | A X | 240 | V ) = | [10 empty] | PER PHASE DEMAND ( | 5,500 | VA ÷ 2 ) = | 2,750 | VA
|  |  | TABLE 220.54 | [15 empty] | 32 |  | 0 | X | 0 | A X | 240 | V ) =
|  |  | 70% OF TABLE 220.54 ( 5,500 VA 1.00 VA X 0.70 ) = |  |  | 3850 |  | UNDERGROUND | [10 empty] | 33 |  | 0 | X | 0 | A X | 240 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 2750 | VA X 3 ) =
[8 empty] | METER | [10 empty] | 34 |  | 0 | X | 0 | A X | 240 | V ) = | [10 empty] | EQUIVALENT 3-PHASE LOAD ( | 2,750 | VA X 3 ) =
|  |  | UNBALANCED MISC LOADS |  |  | 0
0
|  |  | NEUTRAL LOAD VA |  |  | 14550
MISC LOADS NEC 220.82(B)(4)
|  |  | NEUTRAL LOAD ( 14,550 VA ÷ 240 V ) = |  |  | 61
[15 empty] | WIRE CODE | #1
|  |  | FURTHER DEMAND FACTOR - NEC 220.61(B)(2) | [11 empty] | SER | ERROR
|  |  | FIRST 200 A @ 100% (61 A X 1.00 ) = |  |  | 61 |  | FEEDER TYPE | CONDUIT
|  |  | REMAINDER @ 70% ( 0 A X 0.70 ) = |  |  | 0 |  |  | -- | [6 empty] | #1 |  |  |  | WIRE | WIRE | SYSTEM
[20 empty] | SIZE | SIZE | GROUND
|  |  | MINIMUM NEUTRAL CONDUCTOR AMPACITY |  |  | 61 |  | SIZE | 3" | [6 empty] | 5 |  |  |  | AWG | CODE
[8 empty] | CONDUIT | PVC |  | 3" PVC -- |  |  |  |  | --------------------------- |  |  | 1 | #6 | 5 | #8
[8 empty] | DISPLAY | 99 |  | -- 3" PVC |  |  |  |  | #6 |  |  | 2 | #4 | 6 | #8
|  |  | VOLTAGE DROP CALCULATIONS | [15 empty] | 3 | #3 | 6 | #8
|  |  | ( 2 X 10' L X 0.2530 R X 109.0 A ÷ 1,000 ) = 0.6 VD | [5 empty] | UNDERGROUND | [6 empty] | UFER GND |  |  | 4 | #2 | 8 | #8
|  |  | ( 0.6 VD ÷ 240 V X 100 ) = 0.3 % VD |  |  |  |  | 60A-2P | METER | [9 empty] | 5 | #1 | 9 | #6
[9 empty] | MAIN PANEL | [6 empty] | --------------------------- #6 UFER GND |  |  | 6 | #1/0 | 10 | #6
|  |  | FAULT CURRENT CALCULATIONS | [15 empty] | 7 | #2/0 | 11 | #6
|  |  | (( 22,000 AFC X 1.00 UA ) + 0 MC ) = 22,000 AFC |  |  |  |  | FEEDER | [10 empty] | 8 | #3/0 | 12 | #4
|  |  | ( 2 X 10 L X 22,000 AFC ) ÷ ( 4,645 C X 1 N X 240 V ) = 0.395 CF |  |  |  | --- | 25' |  | --- 25' | [8 empty] | 9 | #3/0 | 12 | #4
|  |  | ( 1 ) ÷ ( 1 + 0.395 CF ) = 0.717 CM |  |  |  | --- | 1- SER CABLE |  | --- 1- SER CABLE |  | 1- SER CABLE --- | [6 empty] | 10 | #4/0 | 12 | #4
|  |  | ( 22,000 AFC X 0.717 CM ) = 15,774 CLC |  |  |  |  | 3-#4 AL |  | 3-#4 AL | [8 empty] | 11 | #250 | 12 | #4
[8 empty] | 1-#6 GND |  | 1-#6 GND | [8 empty] | 12 | #300 | 12 | #4
[19 empty] | 13 | #350 | 12 | #4
|  |  |  | KEY | [14 empty] | 14 | #400 | 12 | #4
|  |  |  | A - Amps | [14 empty] | 15 | #500 | 12 | #4
|  |  |  | AFC - Available Fault Current | [14 empty] | 16 | #600 | 12 | #4
|  |  |  | C - Conductor Constance | [14 empty] | 17 | #750 | 12 | #4
PUMP ( 1 X 16 A X 240 V ) = |  | 3840 |  | CF - Conductor Factor |  |  |  | 60A-2P | [10 empty] | 18 | #1000 | 12 | #4
CLC - Conductor Let Through Current
CM - Conductor Multiplier
|  |  |  | L - Length |  |  |  | SP1
MC - Motor Contribution
N - Number of Conductors
R - Resistance
UA - Utility Adjustment
V - Volts
VA - Volt Amps
LARGEST HEATING OR COOLING LOAD |  | 4000 |  | VD - Voltage Drop
TOTAL LOAD |  | 33955
TOTAL AMPS ( 33,955 VA ÷ 240 V ) = |  | 141 | [23 empty] | TEXT
FUTURE AMPS ( 0% ) |  | 0 |  | Prepared With Service Pro 2008 Software | [15 empty] | (1) AC LOAD ( |  |  |  | VA | 4000 | 4,000 | VA X 100% ) = | (1) AC LOAD ( 4,000 VA X 100% ) = 4,000 VA | 4000
DESIGN AMPS |  | 141 |  | Copyright Durand & Associates | [15 empty] | (2) HEAT PUMPS NO SUPP ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (2) HEAT PUMPS NO SUPP ( 0 VA X 100% ) = 0 VA | 0
[20 empty] | (3) HEAT PUMPS ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (3) HEAT PUMPS ( 0 VA X 100% ) = 0 VA | 0 |  |  | SUPPLEMENTAL HEAT ( | 0 | 0 | VA X 65% ) = | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = |  |  |  | 0 | 0 | VA | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = 0 VA
[20 empty] | (4) ELECTRIC SPACE ( |  |  |  | VA | 0 | 0 | VA X 65% ) = | (4) ELECTRIC SPACE ( 0 VA X 65% ) = 0 VA | 0 | 0 |  | (4) ELECTRIC SPACE ( 0 VA X 65% ) = 0 VA
[20 empty] | (5) SPACE HEATING ( |  |  |  | VA | 0 | 0 | VA X 40% ) = | (5) SPACE HEATING ( 0 VA X 40% ) = 0 VA | 0 | 0
[20 empty] | (6) SPACE HEATING ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (6) SPACE HEATING (0 VA X 100% ) = 0 VA | 0 | 0 |  | SUPPLEMENTAL HEAT ( | 0 | 0 | VA X 65% ) = | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = |  |  |  | 0 | 0 | VA | SUPPLEMENTAL HEAT ( 0 VA X 65% ) = 0 VA
4000
[20 empty] | 33955 |  |  |  |  | 33,955 | VA ÷ | 240 | V ) = | 141 |  |  | =
[34 empty] | 1 | 4000 |  | 4000 | 4000 | 1 | 4000
[25 empty] | TOTAL AMPS ( |  |  | TOTAL AMPS ( 33,955 VA ÷ 240 V ) = | [5 empty] | 2 | 0 |  | 0 | 0 | 0 | 0
[20 empty] | NEUTRAL | [13 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | FIRST 3,000 VA @ 100% ( | 3000 |  | 3,000 | VA X 1.00 ) = |  |  |  |  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) = | [5 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0
[34 empty] | 5 | 0 |  | 0 | 0 | 0 | 0
[19 empty] | 3,000-120,000 VA @ 35% ( | 9000 |  | 3000 | 6000 | 6,000 | VA X 0.35 ) = |  |  | 3,000-120,000 VA @ 35% ( 6,000 VA X 0.35 ) = | 2100 |  |  |  |  | 6 | 0 |  | 0 | 0 | 0 | 0
[19 empty] | OVER 120,000 VA @ 25% ( | 0 |  |  | 0 |  | VA X 0.25 ) = |  |  | OVER 120,000 VA @ 25% ( 0 VA X 0.25 ) = | 0 | [10 empty] | 4000
RANGE
[17 empty] | 70% OF TABLE |  | 70% OF TABLE 220.55 ( | 8000 |  |  | 8,000 |  | VA X 0.70 ) = |  |  | 70% OF TABLE 220.55 ( 8,000 VA X 0.70 ) = | 5600
[17 empty] | 70% OF TABLE |  |  | DRYER |  |  |  | 1
[19 empty] | 70% OF TABLE 220.54 ( | 5500 |  |  | 5,500 | 1.00 | VA X 0.70 ) = | VA |  | 70% OF TABLE 220.54 ( 5,500 VA 1.00 VA X 0.70 ) = | 3850 | 3850 | 2695
UNBALANCED
[20 empty] | 0 |  |  | 0 |  | VA X 1.00 = |  |  | 0 VA X 1.00 = | 0
[12 empty] | UNDERGROUND | [7 empty] | NEUTRAL AMPS
[12 empty] | METER | [6 empty] | NEUTRAL LOAD ( | 14550 |  |  | 14,550 |  | VA ÷ | 240 | V ) = | NEUTRAL LOAD ( 14,550 VA ÷ 240 V ) = |  | 61
[8 empty] | >> |  | 1 |  | 0
[9 empty] | VD | 2
[9 empty] | AFC | 3 | [9 empty] | FUTUR AMPS (
[10 empty] | 4 | [9 empty] | 141 |  |  | 141 |  | A X | 0 | = | 141 A X 0 =
[23 empty] | FUTURE AMPS |  | ( | 0 | % ) | FUTURE AMPS ( 0% )
[10 empty] | 4 |  | 1 |  | 2 |  | 3 |  | 4 |  | 5
[10 empty] | A - Amps |  | A - Amps |  | A - Amps |  | A - Amps |  | A - Amps |  | A - Amps
[10 empty] | AFC - Available Fault Current |  | V - Volts |  | L - Length |  | AFC - Available Fault Current |  | AFC - Available Fault Current |  | AFC - Available Fault Current
[10 empty] | C - Conductor Constance |  | VA - Volt Amps |  | R - Resistance |  | C - Conductor Constance |  | C - Conductor Constance |  | MC - Motor Contribution
[10 empty] | CF - Conductor Factor |  |  |  | V - Volts |  | CF - Conductor Factor |  | CF - Conductor Factor |  | UA - Utility Adjustment
[10 empty] | CLC - Conductor Let Through Current |  |  |  | VA - Volt Amps |  | CLC - Conductor Let Through Current |  | CLC - Conductor Let Through Current |  | V - Volts
[10 empty] | CM - Conductor Multiplier |  |  |  | VD - Voltage Drop |  | CM - Conductor Multiplier |  | CM - Conductor Multiplier |  | VA - Volt Amps
[10 empty] | L - Length | [5 empty] | L - Length |  | L - Length
[10 empty] | MC - Motor Contribution | [5 empty] | MC - Motor Contribution |  | MC - Motor Contribution
[10 empty] | N - Number of Conductors | [5 empty] | N - Number of Conductors |  | N - Number of Conductors
[10 empty] | R - Resistance | [5 empty] | UA - Utility Adjustment |  | R - Resistance
[10 empty] | UA - Utility Adjustment | [5 empty] | V - Volts |  | UA - Utility Adjustment
[10 empty] | V - Volts | [5 empty] | VA - Volt Amps |  | V - Volts
[10 empty] | VA - Volt Amps | [7 empty] | VA - Volt Amps
[10 empty] | VD - Voltage Drop | [7 empty] | VD - Voltage Drop

## 1-Line
ERROR | 0
OVER UNDER | UNDERGROUND
METER
MAIN PANEL
SUBPANELS | 6 | [16 empty] | 1-Line Drawing
UPDATE | 0 | [16 empty] | SAMPLE
123 MAIN
FOLSOM, CA 95630
1-1 1/4'' EMT
2-#1 THHN AL
1-#4 THHN AL (N)
1-#4 AL GND
[5 empty] | 22.0 K |  | METER
FAULT YES NO | YES
VD YES NO | YES
|  |  |  | 30' |  |  |  |  | 1-1 1/4'' EMT
|  |  |  | 3" PVC |  |  |  |  | 2-#1 THHN AL
UNDERGROUND |  | 3" PVC | [6 empty] | 1-#4 THHN AL (N)
1-#4 AL GND
[8 empty] | 15.8 K | 0.3 % VD
200A
MAIN
BREAKER
|  |  | \ | /
MAIN PANEL
#8 CU
TO UFER GND
|  |  | ---- | ----
|  |  | --- | ---
|  |  | -- | --
[7 empty] | 25' |  |  |  |  | 25' |  |  | 25' |  |  | 25' |  |  | 25' |  |  | 25'
[7 empty] | 1- SER CABLE |  |  |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE
[7 empty] | 3-#4 AL |  |  |  |  | 3-#4 AL |  |  | 3-#4 AL |  |  | 3-#4 AL |  |  | 3-#4 AL |  |  | 3-#4 AL
[7 empty] | 1-#6 GND |  |  |  |  | 1-#6 GND |  |  | 1-#6 GND |  |  | 1-#6 GND |  |  | 1-#6 GND |  |  | 1-#6 GND
[6 empty] | 6.6 K | 0.4 % VD |  |  |  | 6.6 K | 0.4 % VD |  | 6.6 K | 0.4 % VD |  | 6.6 K | 0.4 % VD |  | 6.6 K | 0.4 % VD |  | 6.6 K | 0.4 % VD
[5 empty] | SP1 |  |  |  |  | SP2 |  |  | SP3 |  |  | SP4 |  |  | SP5 |  |  | SP6

## Tables (hidden)
TABLE 220.55, FROM 2005 N.E.C.
|  | NUMBER |  |  | COLUMN C |  | COLUMN A |  | COLUMN B
|  | OF |  |  | NOT OVER 12 |  | LESS THAN 3.5 |  | 3.5 to 8.75
|  | APPLIANCES |  |  | KW RATING |  | KW RATING |  | KW RATING
1
2008
|  | 1 | 1 | 8 | 8 | 0.8 | 80 | 0.8 | 80 |  |  |  | 1 | 1
NUMBER OF RANGES | 1 | 2 | 2 | 0 | 11 | 0 | 75 | 0 | 65 | RANGE ( | 1 | AT | 12000 | VA )
|  | 3 | 3 | 0 | 14 | 0 | 70 | 0 | 55 | RANGE ( | 1 | AT | 12,000 | VA ) |  |  | RANGE ( 1 AT 12,000 VA )
MAXIMUM DEMAND |  | 4 | 4 | 0 | 17 | 0 | 66 | 0 | 50
FROM COLUMN A |  | 5 | 5 | 0 | 20 | 0 | 62 | 0 | 45 | ( | 8000 | VA X | 1 |  | 8000
TABLE 220-19 | 8 | 6 | 6 | 0 | 21 | 0 | 59 | 0 | 43 | PER TABLE 220.55 ( | 8,000 | VA X | 1.00 | ) = | 8,000 | VA | PER TABLE 220.55 ( 8,000 VA X 1.00 ) = VA
| 8000 | 7 | 7 | 0 | 22 | 0 | 56 | 0 | 40
PERCENTAGE DEMAND |  | 8 | 8 | 0 | 23 | 0 | 53 | 0 | 36 | EQUIVALENT 3-PHASE LOAD ( 12,000 VA X 3 ) =
FROM COLUMN B |  | 9 | 9 | 0 | 24 | 0 | 51 | 0 | 35 | EQUIVALENT 3-PHASE LOAD ( | 8000 | VA X 3 )
TABLE 220.55 | 0.8 | 10 | 10 | 0 | 25 | 0 | 49 | 0 | 34 | EQUIVALENT 3-PHASE LOAD ( | 8,000 | VA X 3 ) |  |  | 16000
|  | 11 | 11 | 0 | 26 | 0 | 47 | 0 | 32
PERCENTAGE DEMAND |  | 12 | 12 | 0 | 27 | 0 | 45 | 0 | 32 | PER PHASE DEMAND ( 30,000 VA ÷ 2 ) = 15,000 VA
FROM COLUMN C |  | 13 | 13 | 0 | 28 | 0 | 43 | 0 | 32 | PER PHASE DEMAND ( | 8000 | ÷ 2 ) =
TABLE 220.55 | 0.8 | 14 | 14 | 0 | 29 | 0 | 41 | 0 | 32
|  | 15 | 15 | 0 | 30 | 0 | 40 | 0 | 32
|  | 16 | 16 | 0 | 31 | 0 | 39 | 0 | 28
|  | 17 | 17 | 0 | 32 | 0 | 38 | 0 | 28
|  | 18 | 18 | 0 | 33 | 0 | 37 | 0 | 28
|  | 19 | 19 | 0 | 34 | 0 | 36 | 0 | 28
|  | 20 | 20 | 0 | 35 | 0 | 35 | 0 | 28
|  | 21 | 21 | 0 | 36 | 0 | 34 | 0 | 26
|  | 22 | 22 | 0 | 37 | 0 | 33 | 0 | 26
|  | 23 | 23 | 0 | 38 | 0 | 32 | 0 | 26
|  | 24 | 24 | 0 | 39 | 0 | 31 | 0 | 26
|  | 25 | 25 | 0 | 40 | 0 | 30 | 0 | 26
|  | 26-30 | 26 | 0 | 15 KW + 1KW | 0 | 30 | 0 | 24
|  | 31-40 | 31 |  | FOR EACH RANGE |  | 30 | 0 | 22
|  | 41-50 | 41 | 0 | 25 KW + .75 KW |  | 30 | 0 | 20
|  | 51-60 | 51 |  | FOR EACH |  | 30 | 0 | 18
|  | 61 & OVER | 61 |  | RANGE |  | 30 | 0 | 16
|  |  |  | 8 |  | 0.8 |  | 0.8
TABLE 220.54, FROM 2005 N.E.C.
|  | NUMBER |  |  | DEMAND |  |  |  |  | 1
|  | OF |  |  | FACTOR
|  | DRYERS |  |  | PERCENT |  |  |  |  | 2008
NUMBER OF DRYERS | 1 | 1 | 1 | 100 | 100 |  |  |  |  | DRYER ( | 1 | AT | 5500 | VA )
|  | 2 | 2 | 0 | 100 |  |  |  |  | DRYER ( | 1 | AT | 5,500 | VA ) |  |  |  |  | DRYER ( 1 AT 5,500 VA )
DEMAND FACTOR | 100 | 3 | 3 | 0 | 100 | [5 empty] | 1 | VA X | 5500 |  | 1 |  | 5500
|  | 4 | 4 | 0 | 100 |  |  |  |  | PER TABLE 220.54 ( | 1 | X | 5,500 | X | 1.00 | ) = | 5,500 | VA | PER TABLE 220.54 ( 1 X 5,500 X 1.00 ) =
|  | 5 | 5 | 0 | 85
|  | 6 | 6 | 0 | 75
| #VALUE! | 7 | 7 | 0 | 65 |  |  |  |  | EQUIVALENT 3-PHASE LOAD ( | 1 | VA X 3 )
|  | 8 | 8 | 0 | 60 |  |  |  |  | EQUIVALENT 3-PHASE LOAD ( | 1 | VA X 3 ) |  |  | 2
|  | 9 | 9 | 0 | 55
|  | 10 | 10 | 0 | 50 |  |  |  |  | PER PHASE DEMAND ( 30,000 VA ÷ 2 ) = 15,000 VA
|  | 11 | 11 | 0 | 47 |  |  |  |  | PER PHASE DEMAND ( | 1 | ÷ 2 ) =
|  | 12 | 12 | 0 | 46 |  | 46 | 46 | 0
|  | 13 | 13 | 0 | 45 |  | 45 | 45 | 0
|  | 14 | 14 | 0 | 44 |  | 44 | 44 | 0
|  | 15 | 15 | 0 | 43 |  | 43 | 43 | 0
|  | 16 | 16 | 0 | 42 |  | 42 | 42 | 0
|  | 17 | 17 | 0 | 41 |  | 41 | 41 | 0
|  | 18 | 18 | 0 | 40 |  | 40 | 40 | 0
|  | 19 | 19 | 0 | 39 |  | 39 | 39 | 0
|  | 20 | 20 | 0 | 38 |  | 38 | 38 | 0
|  | 21 | 21 | 0 | 37 |  | 37 | 37 | 0
|  | 22 | 22 | 0 | 36 |  | 36 | 36 | 0
|  | 23 | 23 | 0 | 35 |  | 35 | 35 | 0
|  | 24 | 24 | 0 | 34.5 |  | 34.5 | 34.5 | 0
|  | 25 | 25 | 0 | 34 |  | 34 | 34 | 0
|  | 26 | 26 | 0 | 33.5 |  | 33.5 | 33.5 | 0
|  | 27 | 27 | 0 | 33 |  | 33 | 33 | 0
|  | 28 | 28 | 0 | 32.5 |  | 32.5 | 32.5 | 0
|  | 29 | 29 | 0 | 32 |  | 32 | 32 | 0
|  | 30 | 30 | 0 | 31.5 |  | 31.5 | 31.5 | 0
|  | 31 | 31 | 0 | 31 |  | 31 | 31 | 0
|  | 32 | 32 | 0 | 30.5 |  | 30.5 | 30.5 | 0
|  | 33 | 33 | 0 | 30 |  | 30 | 30 | 0
|  | 34 | 34 | 0 | 29.5 |  | 29.5 | 29.5 | 0
|  | 35 | 35 | 0 | 29 |  | 29 | 29 | 0
|  | 36 | 36 | 0 | 28.5 |  | 28.5 | 28.5 | 0
|  | 37 | 37 | 0 | 28 |  | 28 | 28 | 0
|  | 38 | 38 | 0 | 27.5 |  | 27.5 | 27.5 | 0
|  | 39 | 39 | 0 | 27 |  | 27 | 27 | 0
|  | 40 | 40 | 0 | 26.5 |  | 26.5 | 26.5 | 0
|  | 41 | 41 | 0 | 26 |  | 26 | 26 | 0
|  | 42 | 42 | 0 | 25.5 |  | 25.5 | 25.5 | 0
|  | 43 & OVER | 43 | 0 | 25 |  | 25 |  | 99
100
RANGE ADD
5% PER KVA
OVER 12
| RANGE RATING | 12 | KVA
0
| 12 | 13 | 0.05
| 13 | 14 | 0.1
| 14 | 15 | 0.15
| 15 | 16 | 0.2
| 16 | 17 | 0.25
| 17 | 18 | 0.3
| 18 | 19 | 0.35
| 19 | 20 | 0.4
| 20 | 21 | 0.45
| 21 | 22 | 0.5
| 22 | 23 | 0.55
| 23 | 24 | 0.6
| 24 | 25 | 0.65
| 25 | 26 | 0.7
| 26 | 27 | 0.75
1
UNBALANCED LOAD
LOAD
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
|  | 0 | 0 |  |  | 0 | 0 | 0
0
0

## Conduit (hidden)
# OF CONDUITS |  |  |  | OPTIONAL
|  | 1 1/4'' |  | EMT | ( | 3 | - | #1 |  |  | 1 | - | CONDUIT | 1 - CONDUIT
CONDUITS | 1 1/4'' | EMT | [8 empty] | 1 1/4'' |  | EMT | 1 1/4'' EMT | [18 empty] | INPUT | EMT
[23 empty] | OVER CURRENT MODULE | [9 empty] | 1. GENERAL | 0 |  | CONDUIT SIZING MODULE
|  |  |  | WIRE SIZE MODULE (4" MAX CONDUIT) | [12 empty] | HIGH VOLTAGE |  | 240 | [13 empty] | 2. RIGID | 0
|  | HI | NEUTRAL | CU/AL? | AL |  |  |  |  | WIRES | [6 empty] | LOW VOLTAGE |  | 120 |  |  |  | FUSE SIZING AMPS | 109 | 0 | [7 empty] | 3. EMT | 3 |  | CONDUIT TYPE | 3
OPT STD | 100 | LEG | AMPS | WIRE TEMP | 75 |  | L2 AMPS |  | 0 | 1 | 0 | [5 empty] | PHASE |  | 1 |  |  |  | # OF PHASE WIRES | 1 | [8 empty] | 4. IMC | 0 |  | WIRE AREA SQ IN | 0.4772
DESIGN AMPS | 109 |  |  | DESIGN AMPS (NDA) | 109 |  | NEUTRAL AMPS |  | 61 | 1 | 61 | [21 empty] | 5. PVC-40 | 0 |  | PERCENT FILL | 0.4
MIN AMPS | 0 |  | 61 | LOOKUP AMPS | 109 |  | 33% OF PHASE |  | 36.7 | 1 | 36.7 | [21 empty] | 6. RIGID/PVC | 0
|  | 0 |  | NET Y/N | Y | 3 | MAX |  | 61 |  | 61 | [11 empty] | LOOKUP | FUSE/BKR | [8 empty] | 7. FLEX | 0 |  | LOOKUP | 40% | CONDUIT | EMT | CONDUIT |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
CONNECTED LOAD |  |  |  | HAR Y/N | N | 0 | [10 empty] | 1 | 1 |  |  |  |  | GROUND | AMP | [8 empty] | 8. LT-FLEX | 0 |  | TABLE | FILL | SIZE | AREA | SIZE |  | SIZE | GENERAL | RIGID | EMT | IMC | PVC-40 | RIGID/PVC | FLEX | LT-FLEX
50% CONNECTED | 0 |  |  | SUBTOTAL |  | 3 | [10 empty] | 109 | [5 empty] | AMPS | RATING | [8 empty] | OUTPUT | 3 |  |  |  |  | SQ IN |  |  |  | AREA | AREA | AREA | AREA | AREA | AREA | AREA | AREA
HARMONIC LOAD | 0 | [21 empty] | 0 | 60 | [11 empty] | 0 | 0.1216 | 0.5 | 0.304 | 0.5 |  |  | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN
| N | [21 empty] | 60 | 70 | [11 empty] | 0.1216 | 0.2132 | 0.75 | 0.533 | 0.75 |  | 0.5 | 0.285 | 0.314 | 0.304 | 0.342 | 0.285 | 0.304 | 0.317 | 0.314
|  |  | ROW | LOOKUP |  |  | ADJUST | SELECTED | WIRE | WIRE | WIRE | 60º C | 75 C | 90º C | ROW | AMPACITY TABLE | [6 empty] | 70 | 80 | [11 empty] | 0.2132 | 0.3456 | 1 | 0.864 | 1 |  | 0.75 | 0.508 | 0.549 | 0.533 | 0.586 | 0.508 | 0.533 | 0.533 | 0.541
|  |  |  | WIRE |  |  | WIRE | WIRE | SIZE | SIZE | PER | AMPS | AMPS | AMPS |  | WIRE | 60º C | 75 C | 90º C | 60º C | 75 C | 90º C | 80 | 90 | [11 empty] | 0.3456 | 0.5984 | 1.25 | 1.496 | 1.25 |  | 1 | 0.817 | 0.888 | 0.864 | 0.959 | 0.832 | 0.864 | 0.817 | 0.872
|  |  |  | AMPS |  |  | AMPS | AMPS | AWG | CODE | PHASE | AL | AL | AL |  | SIZE | AMPS | AMPS | AMPS | AMPS | AMPS | AMPS | 90 | 100 | [11 empty] | 0.5984 | 0.8144 | 1.5 | 2.036 | 1.5 |  | 1.25 | 1.277 | 1.526 | 1.496 | 1.646 | 1.453 | 1.495 | 1.277 | 1.528
|  |  | 101 | 0 |  |  | 50 | 50 | #6 | 5 | 1 | 40 | 50 | 60 | 101 | AWG | CU | CU | CU | AL | AL | AL | 100 | 110 | [11 empty] | 0.8144 | 1.3424 | 2 | 3.356 | 2 |  | 1.5 | 1.857 | 2.071 | 2.036 | 2.223 | 1.986 | 2.036 | 1.857 | 1.979
|  |  | 102 | 50 |  |  | 65 | 65 | #4 | 6 | 1 | 55 | 65 | 75 | 102 | #6 | 55 | 65 | 75 | 40 | 50 | 60 | 110 | 125 | [11 empty] | 1.3424 | 2.3432 | 2.5 | 5.858 | 2.5 |  | 2 | 3.245 | 3.408 | 3.356 | 3.629 | 3.291 | 3.355 | 3.269 | 3.245
|  |  | 103 | 65 |  |  | 75 | 75 | #4 | 6 | 1 | 65 | 75 | 85 | 103 | #4 | 100 | 100 | 100 | 55 | 65 | 75 | 125 | 150 | [11 empty] | 2.3432 | 3.5384 | 3 | 8.846 | 3 |  | 2.5 | 4.695 | 4.866 | 5.858 | 5.135 | 4.695 | 4.788 | 4.909 | 4.879
|  |  | 104 | 75 |  |  | 100 | 100 | #2 | 8 | 1 | 100 | 100 | 100 | 104 | #3 | 110 | 110 | 110 | 65 | 75 | 85 | 150 | 175 | [11 empty] | 3.5384 | 4.618 | 3.5 | 11.545 | 3.5 |  | 3 | 7.069 | 7.499 | 8.846 | 7.922 | 7.268 | 7.393 | 7.069 | 7.475
|  |  | 105 | 100 |  |  | 110 | 110 | #1 | 9 | 1 | 110 | 110 | 115 | 105 | #2 | 125 | 125 | 130 | 100 | 100 | 100 | 175 | 200 | [11 empty] | 4.618 | 5.9012 | 4 | 14.753 | 4 |  | 3.5 | 9.621 | 10.01 | 11.545 | 10.584 | 9.737 | 9.866 | 9.621 | 9.731
|  |  | 106 | 110 |  |  | 125 | 125 | #1/0 | 10 | 1 | 125 | 125 | 135 | 106 | #1 | 150 | 150 | 150 | 110 | 110 | 115 | 200 | 225 | [17 empty] | 4 | 12.554 | 12.833 | 14.753 | 13.631 | 12.554 | 12.73 | 12.566 | 12.692
|  |  | 107 | 125 |  |  | 150 | 150 | #2/0 | 11 | 1 | 150 | 150 | 150 | 107 | #1/0 | 175 | 175 | 175 | 125 | 125 | 135 | 225 | 250 | [11 empty] | CONDUIT SIZE | 1.25 | DIFFERENT SIZE WIRES
|  |  | 108 | 150 |  |  | 175 | 175 | #3/0 | 12 | 1 | 175 | 175 | 175 | 108 | #2/0 | 200 | 200 | 200 | 150 | 150 | 150 | 250 | 300 | [11 empty] | CONDUIT TYPE | EMT
|  |  | 109 | 175 |  |  | 200 | 200 | #4/0 | 13 | 1 | 200 | 200 | 205 | 109 | #3/0 | 225 | 225 | 225 | 175 | 175 | 175 | 300 | 350 | [11 empty] | CONDUIT SIZE | NOT USED | SAME SIZE WIRES
|  |  | 110 | 200 |  |  | 225 | 225 | #250 | 14 | 1 | 225 | 225 | 230 | 110 | #4/0 | 250 | 250 | 260 | 200 | 200 | 205 | 350 | 400 | [11 empty] | CONDUIT SIZE | 1.25 | DIFFERENT SIZE WIRES
|  |  | 111 | 225 |  |  | 250 | 250 | #300 | 15 | 1 | 250 | 250 | 255 | 111 | #250 | 300 | 300 | 300 | 225 | 225 | 230 | 400 | 450 | [11 empty] | # OF WIRES | 4
|  |  | 112 | 250 |  |  | 300 | 300 | #350 | 16 | 1 | 300 | 300 | 300 | 112 | #300 | 300 | 300 | 320 | 250 | 250 | 255 | 450 | 500
| CONDUIT SIZE | 1.25 | 113 | 300 |  |  | 300 | 300 | #400 | 17 | 1 | 300 | 300 | 305 | 113 | #350 | 350 | 350 | 350 | 300 | 300 | 300 | 500 | 600 | [18 empty] | 2: EMT; 3: CONDUIT
|  | 1 1/4'' | 114 | 300 |  |  | 350 | 350 | #500 | 18 | 1 | 350 | 350 | 350 | 114 | #400 | 400 | 400 | 400 | 300 | 300 | 305 | 600 | 700 | [14 empty] | 2-WIRE | 3-WIRE | 4-WIRE |  | 2: AREA; 3: SIZE
|  | 0 | 115 | 350 |  |  | 400 | 400 | #4/0 | 13 | 2 |  |  |  | 115 | #500 | 400 | 400 | 430 | 350 | 350 | 350 | 700 | 800 | [18 empty] | 2: SQ IN
|  | 1 1/4'' | 116 | 400 |  |  | 450 | 450 | #250 | 14 | 2 |  |  |  | 116 | [7 empty] | 800 | 1000 | [11 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0.77849 | 1: 0.1562; 2: 0.1216; 3: 0.5
|  |  | 117 | 450 |  |  | 500 | 500 | #300 | 15 | 2 |  |  |  | 117 | [7 empty] | 1000 | 1200 | [11 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1.3649 | 1: 0.1562; 2: 0.2132; 3: 0.75
|  |  | 118 | 500 |  |  | 600 | 600 | #350 | 16 | 2 |  |  |  | 118 | AMPACITY TABLE | [19 empty] | 3 | 0 | 0 | 2 | 0 | 0 | 2.2125 | 1: 0.1562; 2: 0.3456; 3: 1
|  |  | 119 | 600 |  |  | 600 | 600 | #400 | 17 | 2 |  |  |  | 119 | WIRE | 60º C | 75 C | 90º C | 60º C | 75 C | 90º C | [13 empty] | 4 | 4 | 4 | 0 | 3 | 4 | 3.831 | 1: 0.1562; 2: 0.5984; 3: 1.25
|  |  | 120 | 600 |  |  | 700 | 700 | #500 | 18 | 2 |  |  |  | 120 | SIZE | AMPS | AMPS | AMPS | AMPS | AMPS | AMPS | UNDER 800A | 110 | #N/A | [10 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 5.2138 | 1: 0.1562; 2: 0.8144; 3: 1.5
|  |  | 121 | 700 |  |  | 750 | 750 | #300 | 15 | 3 |  |  |  | 121 | AWG | CU | CU | CU | AL | AL | AL | OVER 800A |  | 0 | [10 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 8.5941 | 1: 0.1562; 2: 1.3424; 3: 2
|  |  | 122 | 750 |  |  | 900 | 900 | #350 | 16 | 3 |  |  |  | 122 | #6 | 55 | 65 | 75 | 40 | 50 | 60 | RATING | 110 |  |  | 110 | A-2P |  | 110A-2P | [5 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 15.0013 | 1: 0.1562; 2: 2.3432; 3: 2.5
|  |  | 123 | 900 |  |  | 900 | 900 | #400 | 17 | 3 |  |  |  | 123 | #4 | 70 | 85 | 95 | 55 | 65 | 75 | HI LEG FUSE | [12 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 22.653 | 1: 0.1562; 2: 3.5384; 3: 3
|  |  | 124 | 900 |  |  | 1050 | 1050 | #500 | 18 | 3 |  |  |  | 124 | #3 | 85 | 100 | 110 | 65 | 75 | 85 | [13 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 29.5647 | 1: 0.1562; 2: 4.618; 3: 3.5
|  |  | 125 | 1050 |  |  | 1200 | 1200 | #350 | 16 | 4 |  |  |  | 125 | #2 | 95 | 115 | 130 | 75 | 90 | 100 | [13 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 37.7798 | 1: 0.1562; 2: 5.9012; 3: 4
|  |  | 126 | 1200 |  |  | 1200 | 1200 | #400 | 17 | 4 |  |  |  | 126 | #1 | 110 | 130 | 150 | 85 | 100 | 115 | WIRE FILL SIZING MODULE
|  |  | 127 | 1200 |  |  | 1400 | 1400 | #500 | 18 | 4 |  |  |  | 127 | #1/0 | 125 | 150 | 170 | 100 | 120 | 135 |  | L1 | [12 empty] | 4 | [5 empty] | 1: L2 RESISTANCE CALCULATION
|  |  | 128 | 1400 |  |  | 1500 | 1500 | #350 | 16 | 5 |  |  |  | 128 | #2/0 | 145 | 175 | 195 | 115 | 135 | 150 | WIRE CODE (NPHC) | 9 | [12 empty] | 1.25
|  |  | 129 | 1500 |  |  | 1500 | 1500 | #400 | 17 | 5 |  |  |  | 129 | #3/0 | 165 | 200 | 225 | 130 | 155 | 175 | WIRE TYPE (NWTYP) | THHN | [18 empty] | 1 | 1 | / | 0.253 | = | 0
|  |  | 130 | 1500 |  |  | 1750 | 1750 | #500 | 18 | 5 |  |  |  | 130 | #4/0 | 195 | 230 | 260 | 150 | 180 | 205 | CU/AL ? | AL | [18 empty] | 2 | 1 | / | 0.253 | = | 0
|  |  | 131 | 1750 |  |  | 1800 | 1800 | #400 | 17 | 6 |  |  |  | 131 | #250 | 215 | 255 | 290 | 170 | 205 | 230 | GND WIRE CODE | 6 | [18 empty] | 3 | 1 | / | 0.253 | = | 0
|  |  | 132 | 1800 |  |  | 2100 | 2100 | #500 | 18 | 6 |  |  |  | 132 | #300 | 240 | 285 | 320 | 190 | 230 | 255 | NEUTRAL Y/N | 0 | 0 | [17 empty] | 4 | 1 | / | 0.253 | = | 0
|  |  |  | OUTPUT | OUTPUT | OUTPUT | OUTPUT | [8 empty] | #350 | 260 | 310 | 350 | 210 | 250 | 280 | #OF WIRE | 3 | 3 | [17 empty] | 5 | 1 | / | 0.253 | = | 0
|  |  |  | SELECTED | WIRE | WIRE | WIRE | [8 empty] | #400 | 280 | 335 | 380 | 225 | 270 | 305 | TOTAL WIRES |  | 3 | [17 empty] | 6 | 1 | / | 0.253 | = | 0
|  |  |  | WIRE | SIZE | SIZE | PER | [8 empty] | #500 | 320 | 380 | 430 | 260 | 310 | 350 | GND WIRE CODE
|  |  |  | AMPS | AWG | CODE | PHASE | [28 empty] | VOLTAGE DROP MODULE | [6 empty] | PARALLEL CONDUCTORS |  |  | 1 | / | 0 | = | 0
|  |  | L1-L3 | 110 | #1 | 9 | 1 |  | HI LEG | [13 empty] | WIRE | WIRE | ST |  | WIRE | WIRE | ST | ST | ST | ST | CA | CA | CA |  | 1-PHASE | 3Y
|  |  | L2 | 110 | #1 | 9 | 1 |  | 50 | #6 | 5 |  |  |  |  | TABLE 310.15(B)(6) | [6 empty] | SIZE | SIZE | THHN |  | WIRE | WIRE | THW | RHW | THHN | XHHW | THW-CA | THHN-CA | XHHW-CA | CU/AL? | AL | [5 empty] | 1: SINGLE CONDUCTOR; 8: 0.253
|  |  | NETURAL | 65 | #4 | 6 | 1 |  | 50 | #6 | 5 |  |  |  |  | WIRE | 60º C | 75 C | 90º C | 60º C | 75 C | 90º C | AWG | CODE | SIZE |  | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | ONE WAY DISTANCE | 10
|  |  |  | 105 | [11 empty] | SIZE | AMPS | AMPS | AMPS | AMPS | AMPS | AMPS |  |  | SQ IN |  | AWG | CODE | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | TOTAL LOAD | 109 | 109 |  |  |  |  | 1: CALCULATED RESISTANCE OF CONDUCTOR(S); 8: 0.253
[9 empty] | NEUTRAL | [6 empty] | AWG | CU | CU | CU | AL | AL | AL | #10 | 3 | 0.0211 |  | #10 | 3 | 0.0333 | 0.0333 | 0.0211 | 0.0243 | 0.051 | 0.051 | 0.0394 | VOLTAGE | 240
|  |  |  | GROUND SIZE MODULE |  |  |  |  | 65 | #4 | 6 |  |  |  |  | #6 | 55 | 65 | 75 | 40 | 50 | 60 | #8 | 4 | 0.0366 |  | #8 | 4 | 0.0556 | 0.0556 | 0.0366 | 0.0437 | 0.051 | 0.051 | 0.0394 | # OF PHASE WIRES | 1
|  |  |  | GND Y/N? (NGYN) | YES |  |  |  | 65 | #4 | 6 |  |  |  |  | #4 | 100 | 100 | 100 | 55 | 65 | 75 | #6 | 5 | 0.0507 |  | #6 | 5 | 0.0726 | 0.1041 | 0.0507 | 0.059 | 0.066 | 0.0452 | 0.0394 | WIRE CODE | 9 | 9 | 9 | 9
|  |  |  | MAX AMPS (NMA) | 110 | [10 empty] | #3 | 110 | 110 | 110 | 65 | 75 | 85 | #4 | 6 | 0.0824 |  | #4 | 6 | 0.0973 | 0.1333 | 0.0824 | 0.0814 | 0.0881 | 0.073 | 0.053 | WIRE | WIRE | RES | RES | RES |  |  | 1: L1 & L2 RESISTANCE CALCULATION
|  |  |  | CU/AL? (NCUAL2) | AL | [10 empty] | #2 | 125 | 125 | 130 | 100 | 100 | 100 | #3 | 7 | 0.0973 |  | #3 | 7 | 0.1134 | 0.1521 | 0.0973 | 0.0962 |  |  |  | SIZE | SIZE | NEC | NEC | NEC
|  |  |  | GND_TABLE | [11 empty] | #1 | 150 | 150 | 150 | 110 | 110 | 115 | #2 | 8 | 0.1158 |  | #2 | 8 | 0.1333 | 0.175 | 0.1158 | 0.1146 | 0.1194 | 0.1017 | 0.073 | AWG | CODE | AL | CU | AL |  |  | 1 | 1 | / | 0.253 | = | 0
|  |  |  | LOOKUP |  | RATING | SEL | SEL |  | RATING | CU | CU | AL | AL |  | #1/0 | 175 | 175 | 175 | 125 | 125 | 135 | #1 | 9 | 0.1562 |  | #1 | 9 | 0.1901 | 0.266 | 0.1562 | 0.1534 | 0.1698 | 0.1352 | 0.1017 | #6 | 5 | 0.808 | 0.491 | 0.808 |  |  | 2 | 1 | / | 0.253 | = | 0
|  |  |  | GROUND |  | OVER | WIRE | WIRE |  | OVER | WIRE | WIRE | WIRE | WIRE |  | #2/0 | 200 | 200 | 200 | 150 | 150 | 150 | #1/0 | 10 | 0.1855 |  | #1/0 | 10 | 0.2223 | 0.3039 | 0.1855 | 0.1825 | 0.1963 | 0.159 | 0.1352 | #4 | 6 | 0.508 | 0.308 | 0.508 |  |  | 3 | 1 | / | 0.253 | = | 0
|  |  |  | AMPS |  | CURRENT | SIZE | CODE |  | CURRENT | SIZE | CODE | SIZE | CODE |  | #3/0 | 225 | 225 | 225 | 175 | 175 | 175 | #2/0 | 11 | 0.2223 |  | #2/0 | 11 | 0.2624 | 0.3505 | 0.2223 | 0.219 | 0.2332 | 0.1924 | 0.159 | #3 | 7 | 0.403 | 0.245 | 0.403 |  |  | 4 | 1 | / | 0.253 | = | 0
|  |  |  | 0 |  | 60 | #8 | 4 |  | 60 | #10 | 3 | #8 | 4 |  | #4/0 | 250 | 250 | 260 | 200 | 200 | 205 | #3/0 | 12 | 0.2679 |  | #3/0 | 12 | 0.3117 | 0.4072 | 0.2679 | 0.2642 | 0.2733 | 0.229 | 0.1885 | #2 | 8 | 0.319 | 0.194 | 0.319 |  |  | 5 | 1 | / | 0.253 | = | 0
|  |  |  | 60 |  | 100 | #6 | 5 |  | 100 | #8 | 4 | #6 | 5 |  | #250 | 300 | 300 | 300 | 225 | 225 | 230 | #4/0 | 13 | 0.3237 |  | #4/0 | 13 | 0.3718 | 0.4754 | 0.3237 | 0.3197 | 0.3267 | 0.278 | 0.229 | #1 | 9 | 0.253 | 0.154 | 0.253 |  |  | 6 | 1 | / | 0.253 | = | 0
|  |  |  | 100 |  | 200 | #4 | 6 |  | 200 | #6 | 5 | #4 | 6 |  | #300 | 300 | 300 | 320 | 250 | 250 | 255 | #250 | 14 | 0.397 |  | #250 | 14 | 0.4596 | 0.6291 | 0.397 | 0.3904 | 0.4128 | 0.3525 | 0.2733 | #1/0 | 10 | 0.201 | 0.122 | 0.201
|  |  |  | 200 |  | 300 | #2 | 8 |  | 300 | #4 | 6 | #2 | 8 |  | #350 | 350 | 350 | 350 | 300 | 300 | 300 | #300 | 15 | 0.4608 |  | #300 | 15 | 0.5281 | 0.7088 | 0.4608 | 0.4536 | 0.4717 | 0.4071 | 0.3421 | #2/0 | 11 | 0.159 | 0.0967 | 0.159 |  |  | PARALLEL CONDUCTORS |  |  | 1 | / | 0 | = | 0
|  |  |  | 300 |  | 400 | #1 | 9 |  | 400 | #3 | 7 | #1 | 9 |  | #400 | 400 | 400 | 400 | 300 | 300 | 305 | #350 | 16 | 0.5242 |  | #350 | 16 | 0.5958 | 0.787 | 0.5242 | 0.5166 | 0.5281 | 0.4656 | 0.4015 | #3/0 | 12 | 0.126 | 0.0766 | 0.126
|  |  |  | 400 |  | 500 | #1/0 | 10 |  | 500 | #2 | 8 | #1/0 | 10 |  | #500 | 400 | 400 | 430 | 350 | 350 | 350 | #400 | 17 | 0.5863 |  | #400 | 17 | 0.6619 | 0.8626 | 0.5863 | 0.5782 | 0.5876 | 0.5216 | 0.4536 | #4/0 | 13 | 0.1 | 0.0608 | 0.1 |  |  | 1: SINGLE CONDUCTOR; 8: 0.253
|  |  |  | 500 |  | 600 | #2/0 | 11 |  | 600 | #1 | 9 | #2/0 | 11 | [8 empty] | #500 | 18 | 0.7073 |  | #500 | 18 | 0.7901 | 1.0082 | 0.7073 | 0.6984 | 0.6939 | 0.6151 | 0.5026 | #250 | 14 | 0.0847 | 0.0515 | 0.0847
|  |  |  | 600 |  | 800 | #3/0 | 12 |  | 800 | #1/0 | 10 | #3/0 | 12 | [21 empty] | #300 | 15 | 0.0707 | 0.0429 | 0.0707 |  |  | 1: CALCULATED RESISTANCE OF CONDUCTOR(S); 8: 0.253
|  |  |  | 800 |  | 1000 | #4/0 | 13 |  | 1000 | #2/0 | 11 | #4/0 | 13 | [8 empty] | L1-L3 WIRE CODE | 9 |  | L1,L3 | L2 | NET | # OF WIRES | [6 empty] | #350 | 16 | 0.0605 | 0.0367 | 0.0605
|  |  |  | 1000 |  | 1200 | #250 | 14 |  | 1200 | #3/0 | 12 | #250 | 14 | [8 empty] | L1-L3 SQ IN | 0.1562 | X | 2 |  |  | 2 | = | 0.3124 | 0.1562 | 0 | 1 | #1 | #400 | 17 | 0.0529 | 0.0321 | 0.0529
|  |  |  | OUTPUT | OUTPUT | OUTPUT | OUTPUT | [15 empty] | L2 WIRE CODE | 9 | [11 empty] | #500 | 18 | 0.0424 | 0.0258 | 0.0424
|  |  |  | GROUND | WIRE | WIRE | WIRE | [15 empty] | L2 SQ IN | 0.1562 | X |  | 0 |  | 0 | = | 0 | 0.1562 | 0 | 3 | #1 | WIRE CODE | 9 | 9 | 9 | 9
|  |  |  | MAX | SIZE | SIZE | PER | [15 empty] | NET WIRE CODE | 6 | [11 empty] | WIRE RES | 0.253 | 0.253 | 0.253 | 0.253
|  |  |  | OVER CURRENT | AWG | CODE | PHASE | [15 empty] | NET SQ IN | 0.0824 | X |  |  | 1 | 1 | = | 0.0824 | 0.0824 | 3 | 4 | #4 | AMPS PER WIRE | 109 | 109 | 0 | 0
|  |  |  | 200 | #4 | 6 | 1 | [15 empty] | GND WIRE CODE | 6
[23 empty] | GND SQ IN | 0.0824 | X |  |  |  | 1 | = | 0.0824 | 0.0824 | 5 | 0 | #4
[23 empty] | TOTAL AREA OF CONDUCTORS | [5 empty] | 4 |  | 0.4772 |  | 8 | 8 | [8 empty] | 3: ( 2 X 10' L X 0.2530 R X 0.0 A ÷ 1,000 ) = 0.0 VD
[29 empty] | AL | (L2) | (N)
[25 empty] | 2 | - | #1 |  | THHN | 2-#1 THHN AL | [8 empty] | 3D | 3D |  |  | 5: VD %; 6: VD %; 7: VD %; 8: VD %
[25 empty] | 0 | - |  |  | THHN | [7 empty] | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3-PHASE Y | L2 | L1 & L3
[25 empty] | 1 | - | #4 |  | THHN | 1-#4 THHN AL (N) | [5 empty] | 2 | 2 | 2 | 2 | 2 | ( | ( | bar: 1 to 8
[25 empty] | 1 | - | #4 |  | GND | 1-#4 AL GND | [5 empty] | X L | 10 | 10 | 10 | 10 | 2 | 2 | 2 | 2 | 2 | VD | 0.6 | 0.5 | 0.0 | 0.0
[36 empty] | X R | 0.253 | 0.253 | 0.253 | 0.253 | X | X | X | X | X | ÷ | VD ÷ | VD ÷ | VD ÷ | VD ÷
[36 empty] | X I | 109 | 109 | 0 | 0 | L | 10 | 10 | 10 | 10 | VOLTS | 240 | 240 | 240 | 240
[30 empty] | 2-#1 THHN AL | [5 empty] | = |  |  |  |  | X | ' L X | ' L X | ' L X | ' L X | X | V X | V X | V X | V X
[30 empty] | 1-#4 THHN AL (N) | [5 empty] | ÷ 1000 | 1000 | 1000 | 1000 | 1000 | R | 0.2530 | 0.2530 | 0.2530 | 0.2530 | 100 | 100 | 100 | 100 | 100
[30 empty] | 1-#4 AL GND | [5 empty] | = |  |  |  |  | X | R X | R X | R X | R X | ) = | ) = | ) = | ) = | ) =
[36 empty] | X 0.866 | 1 | 0.866 | 0.866 | 1 | I | 109.0 | 109.0 | 0.0 | 0.0 | VD | 0.3 | 0.2 | 0.0 | 0.0
[36 empty] | = VD | 0.6 | 0.5 | 0 | 0 | / | A ÷ | A ÷ | A ÷ | A ÷ | % | % VD | % VD | % VD | % VD
[36 empty] | ÷ VOLTS | 240 | 240 | 240 | 240 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | ( VD ÷ VOLTS X 100 ) = VD % | ( 0.6 VD ÷ 240 V X 100 ) = 0.3 % VD | ( 0.5 VD ÷ 240 V X 100 ) = 0.2 % VD | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
[36 empty] | = VD % | 0.25% | 0.21% | 0% | 0% | ) | ) | X | X | ) |  | 0.3 % VD | 0.2 % VD | 0.0 % VD | 0.0 % VD
[25 empty] | 1 | - | 1 1/4'' |  | EMT | 1-1 1/4'' EMT | [10 empty] | 0.866 | = | 1: 0.866; 2: 0.866; 3: =
[30 empty] | 2-#1 THHN AL | [10 empty] | ) | 0.6 | 1: ); 2: ); 3: 0.0; 6: 1
| FEEDER CONDUIT | [28 empty] | 1-#4 THHN AL (N) | [10 empty] | = | VD | = | = | VD |  |  | 0.3 % VD | 0.3 % VD
[30 empty] | 1-#4 AL GND | [10 empty] | VD |  | 1: 0.5; 2: 0.0
| 0 | [25 empty] | FEEDER PER TABLE 310.15(B)(6) | bar: 1 to 2
[23 empty] | FEEDER PER TABLE 310.16 - |  |  |  | FEEDER PER TABLE 310.16 - 75° C
[23 empty] | 75 |  |  |  | FEEDER PER TABLE 310.15(B)(6) |  |  | FEEDER PER TABLE 310.15(B)(6) | [11 empty] | 0.6 VD | 1: 0.5 VD; 2: 0.0 VD; 3: 0.0 VD
[23 empty] | ° C | [18 empty] | ( 2 X 10' L X 0.2530 R X 109.0 A ÷ 1,000 ) = 0.6 VD | 1: ( 2 X 10' L X 0.2530 R X 109.0 A ÷ 1,000 X 0.866 ) = 0.5 VD; 2: ( 2 X 10' L X 0.2530 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD; 3: ( 2 X 10' L X 0.2530 R X 0.0 A ÷ 1,000 ) = 0.0 VD
[23 empty] | FEEDER PER TABLE 310.16 - 75° C | [9 empty] | WIRE | WIRE | [6 empty] | UNDERGROUND
[33 empty] | SIZE | WIRE | [6 empty] | METER
[33 empty] | CODE | SIZE
[34 empty] | AWG | [6 empty] | 0
[33 empty] | 3 | #10
[33 empty] | 4 | #8
[33 empty] | 5 | #6 | [5 empty] | VOLTAGE DROP
[33 empty] | 6 | #4 | [5 empty] | Single Phase | ( 2 X 10' L X 0.2530 R X 109.0 A ÷ 1,000 ) = 0.6 VD |  | 2: Voltage Drop %; 3: ( 0.6 VD ÷ 240 V X 100 ) = 0.3 % VD
[33 empty] | 7 | #3 | [5 empty] | Three Phase | ( 2 X 10' L X 0.2530 R X 109.0 A ÷ 1,000 X 0.866 ) = 0.5 VD |  | 2: Voltage Drop %; 3: ( 0.5 VD ÷ 240 V X 100 ) = 0.2 % VD
[33 empty] | 8 | #2 | [5 empty] | Voltage Drop L1 & L3 | ( 2 X 10' L X 0.2530 R X 0.0 A ÷ 1,000 ) = 0.0 VD |  | 2: Voltage Drop % L1 & L3; 3: ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
[33 empty] | 9 | #1 | [5 empty] | Voltage Drop L2 ( Hi-Leg ) | ( 2 X 10' L X 0.2530 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD |  | 2: Voltage Drop % L2 ( Hi-Leg ); 3: ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
[33 empty] | 10 | #1/0
[33 empty] | 11 | #2/0
[33 empty] | 12 | #3/0
[33 empty] | 13 | #4/0
[33 empty] | 14 | #250
[33 empty] | 15 | #300
[33 empty] | 16 | #350
[33 empty] | 17 | #400
[33 empty] | 18 | #500

## Short (hidden)
NO TRANSFORMER 3-PHASE Y
|  | AFC at Starting Point |  |  | (( | 22000 | AFC x | 1 | UA ) + | 0 | MC ) = | 22000 | AFC
[5 empty] | (( | 22,000 | AFC X | 1.00 | UA ) + | 0 | MC ) = | 22,000 | AFC |  |  |  | (( 22,000 AFC X 1.00 UA ) + 0 MC ) = 22,000 AFC
22,000 AFC
Start > | < 22,000 AFC |  |  |  | < | 22,000 | AFC
[14 empty] | 0.75 | 3/4"
| < ' ' LENGTH |  |  |  | < |  | ' | LENGTH | [5 empty] | 1 | 1" | [8 empty] | CONDUIT
| - | [5 empty] | - | [6 empty] | 1.25 | 1 1/4" |  | UNDERGROUND
| - | [5 empty] | - | [6 empty] | 1.5 | 1 1/2" |  | METER | [5 empty] | GENERAL | 0
[14 empty] | 2 | 2" | [7 empty] | RIGID | 0
[14 empty] | 2.5 | 2 1/2" |  | 0 | [5 empty] | EMT | 1
[14 empty] | 3 | 3" | [7 empty] | IMC | 0
[14 empty] | 3.5 | 3 1/2" | [7 empty] | PVC-40 | 0
End > | < 15,774 AFC |  |  |  | < | 15,774 | AFC | [6 empty] | 4 | 4" | [7 empty] | RIGID/PVC | 0
[23 empty] | FLEX | 0
[23 empty] | LT-FLEX | 0
0
| Step 4 - Conductor Factor CF - Formula | [21 empty] | STELL=1 PLASTIC=2 | 1
| Three Phase | [21 empty] | CU=1 AL=2 | 2
Conductor Factor CF - Formula | ( | 2 | x | 10 | L x | 22000 | AFC ) ÷ ( | 4645 | C x | 1 | N x | 240 | V ) = | 0.395 |  | CF | Print
| ( | 2 | X | 10 | L X | 22,000 | AFC ) ÷ ( | 4,645 | C X | 1 | N X | 240 | V ) = | 0.395 |  | CF | ( 2 X 10 L X 22,000 AFC ) ÷ ( 4,645 C X 1 N X 240 V ) = 0.395 CF | [5 empty] | TOTAL | 3
Step 5 - Conductor Multiplier CM - Formula
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 0.395 | CF ) = | 0.717 | CM | [7 empty] | Print
| ( | 1 | ) ÷ ( | 1 | + | 0.395 | CF ) = | 0.717 | CM | [7 empty] | ( 1 ) ÷ ( 1 + 0.395 CF ) = 0.717 CM
3
Step 6 - Conductor Let-Through Current CLC - Formula
Conductor Let-Through Current CLC - Formula | ( | 22000 | AFC X | 0.717 | CM ) = | 15774 | CLC | [9 empty] | Print | [5 empty] | 3 |  | 1 | 2 | 3 | 4 | 5 | 6
| ( | 22,000 | AFC X | 0.717 | CM ) = | 15,774 | CLC |  |  | 15,774 CLC | [6 empty] | ( 22,000 AFC X 0.717 CM ) = 15,774 CLC | [5 empty] | Steel Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit | SER-ROMEX | SER-ROMEX
[23 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | CABLE | CABLE
|  |  | ( 22,000 AFC X 0.717 CM ) = 15,774 CLC | [15 empty] | C7 | #1 | 9 |  | Cables AL |  | Cables CU | Cables CU | Cables AL | Cables AL | CU | AL
[18 empty] | #1 |  |  |  | 1 | 237 | #14 | 389 | 389 | 237 | 237 | 389 | 237
[6 empty] | 15.8 | [11 empty] | ERROR |  |  |  | 2 | 376 | #12 | 617 | 617 | 376 | 376 | 617 | 376
[6 empty] | 15.8 | K |  |  | 15.8 K | [11 empty] | 3 | 599 | #10 | 981 | 982 | 599 | 599 | 982 | 599
[22 empty] | 4 | 951 | #8 | 1557 | 1559 | 951 | 952 | 1560 | 952
[6 empty] | 22 | [15 empty] | 5 | 1481 | #6 | 2425 | 2430 | 1481 | 1482 | 2433 | 1482
[6 empty] | 22.0 | K |  |  | 22.0 K | [11 empty] | 6 | 2346 | #4 | 3806 | 3826 | 2346 | 2350 | 3838 | 2353
[22 empty] | 7 | 2952 | #3 | 4774 | 4811 | 2952 | 2961 | 4833 | 2966
[22 empty] | 8 | 3713 | #2 | 5907 | 6044 | 3713 | 3730 | 6087 | 3740
[21 empty] | 9 | 9 | 4645 | #1 | 7293 | 7493 | 4645 | 4678 | 7579 | 4699
[22 empty] | 10 | 5777 | #1/0 | 8925 | 9317 | 5777 | 5838 | 9473 | 5876
[22 empty] | 11 | 7187 | #2/0 | 10755 | 11424 | 7187 | 7301 | 11703 | 7373
[22 empty] | 12 | 8826 | #3/0 | 12844 | 13923 | 8826 | 9110 | 14410 | 9243
[22 empty] | 13 | 10741 | #4/0 | 15082 | 16673 | 10741 | 11174 | 17438 | 11409
[22 empty] | 14 | 12122 | #250 | 16483 | 18594 | 12122 | 12862 | 19779 | 13236
[22 empty] | 15 | 13910 | #300 | 18177 | 20868 | 13910 | 14923 | 22525 | 15495
[22 empty] | 16 | 15484 | #350 | 19704 | 22737 | 15484 | 16813 | 24904 | 17635
[22 empty] | 17 | 16671 | #400 | 20566 | 24297 | 16671 | 18506 | 26916 | 19588
[22 empty] | 18 | 18756 | #500 | 22185 | 26706 | 18756 | 21391 | 30096 | 23018
[22 empty] | 4645 | #1

## S-Sec Cable (hidden)
7
TABLE 310.15(B)(6) | YES | 7
HIGH VOLTAGE | 240 | [11 empty] | TABLE
LOW VOLTAGE | 120 | [5 empty] | SHORT | WIRE | WIRE | GROUND | MAX |  | 310.15 |  |  | 3-COND W/GND SER CABLE AL
PHASE | 1 | [5 empty] | C VALUE | RES | SIZE | SIZE | AMPS | [15 empty] | TABLE | AMPACITY TABLE
AMPS | 109 | 0 | SER 3C AL | SER CABLE | 3-#1 AL | 1-#3 GND | 4699 | 0.253 | #1 | #3 | 110 | 1-1-1-3 | 1 | AMPS | 109 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | 310.15(B)(6) | WIRE | 60º C | 75 C | 90º C | TABLE
WIRE TEMP | 75 | 0 | SER 3C CU | SER CABLE | 3-#3 CU | 1-#5 GND | 4833 | 0.245 | #3 | #5 | 110 | 3-3-3-5 | 1 | WIRE TEMP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | AMPS | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
# OF CONDUCTORS | 3 | 0 | SER 4C AL | SER CABLE | 4-#1 AL | 1-#3 GND | 4699 | 0.253 | #1 | #3 | 110 | 1-1-1-1-3 | 1 | [5 empty] | AWG |  |  | AL | NUMBER |  |  | AL |  | AWG | AL | AL | AL
CU OR AL | AL | 0 | ROMEX 3C CU | ROMEX | 3-#2 CU | 1-#8 GND | 4833 | 0.194 | #2 | #8 | 115 | 2-2-2-2 |  |  |  |  | 100 | 0 | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 |  | #6 | 40 | 50 | 60
FEEDER TYPE | CONDUIT | 0 | MC 3C AL | MC CABLE | 3-#1 AL | 1-#4 GND | 4686 | 0.253 | #1 | #4 | 110 | 1-1-1-4 | 1 |  |  |  | 101 | 50 | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 |  | #4 | 55 | 65 | 75
|  | 0 | MC 4C AL | MC CABLE | 4-#1 AL | 1-#4 GND | 4686 | 0.253 | #1 | #4 | 110 | 1-1-1-1-4 | 1 |  |  |  | 102 | 65 | 2-2-2-4 | #2 | #4 | 100 | 8 | 102 | 3740 | 0.319 |  | #2 | 100 | 100 | 100 | 100 | 0 | 0
|  | 0 | MC 3C CU | MC CABLE | 3-#3 CU | 1-#6 GND | 4820 | 0.245 | #3 | #6 | 110 | 3-3-3-6 | 1 |  |  |  | 103 | 100 | 1-1-1-3 | #1 | #3 | 110 | 9 | 103 | 4699 | 0.253 |  | #1 | 110 | 110 | 115 | 110 | 0 | 1
| YES | 0 | MC 4C CU | MC CABLE | 4-#3 CU | 1-#6 GND | 4820 | 0.245 | #3 | #6 | 110 | 3-3-3-3-6 | 1 |  |  |  | 104 | 110 | 1/0-1/0-1/0-2 | #1/0 | #2 | 125 | 10 | 104 | 5876 | 0.201 |  | #1/0 | 125 | 125 | 135 | 125 | 0 | 0
| 240 | [15 empty] | 105 | 125 | 2/0-2/0-2/0-1 | #2/0 | #1 | 150 | 11 | 105 | 7373 | 0.159 |  | #2/0 | 150 | 150 | 150 | 150 | 0 | 0
| 120 | [15 empty] | 106 | 150 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 175 | 12 | 106 | 9243 | 0.126 |  | #3/0 | 175 | 175 | 175 | 175 | 0 | 0
| 1 |  | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR |  |  |  | 107 | 175 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 200 | 13 | 107 | 11409 | 0.1 |  | #4/0 | 200 | 200 | 205 | 200 | 0 | 0 |  | 1
| 125 | [15 empty] | 108 | 200 | EXCEED | EXCEED | EXCEED | 200 | EXCEED | 108 | EXCEED | EXCEED
| 75 |  | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | [14 empty] | #1/0 | 100 | 120
| 3 | [12 empty] | - FEEDER PER TABLE 310.16 - |  |  | 103 |  | 1-1-1-3 | #1 | #3 | 110 | 9 | 103 | 4699 | 0.253 |  | #2/0 | 115 | 135
| CU | [12 empty] | - FEEDER PER TABLE 310.15(B)(6) | [13 empty] | #3/0 | 130 | 155
| SER | [12 empty] | 75 |  |  |  |  | SER CABLE |  |  |  |  | SER CABLE |  |  |  | #4/0 | 150 | 180
[14 empty] | ° C |  |  |  |  | 3- | #1 | AL |  |  | 3-#1 AL
|  |  | THE DESIGN LOAD OF | 109 | AMPS EXCEEDS THE |  |  |  | THE DESIGN LOAD OF 109 AMPS EXCEEDS THE | [9 empty] | 1- | #3 | GND |  |  | 1-#3 GND
|  |  | MAXIMUM CABLE RATING OF | ERROR | AMPS |  |  |  | MAXIMUM CABLE RATING OF ERROR AMPS |  |  |  |  | - FEEDER PER TABLE 310.16 - 75° C
3-COND W/GND SER CABLE CU
|  |  | 1- | ERROR |  |  |  | 1-ERROR | [19 empty] | AMPACITY TABLE
|  |  | ERROR |  |  |  |  | ERROR | [5 empty] | AMPS | 109 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
|  |  | ERROR |  |  |  |  | ERROR |  |  |  | ° |  | WIRE TEMP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | CU | NUMBER |  |  | CU |  | AWG | CU | CU | CU
[17 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 65 | 5 | 100 | 2433 | 0.491 |  | #6 | 55 | 65 | 75
[17 empty] | 101 | 65 | 4-4-4-6 | #4 | #6 | 100 | 6 | 101 | 3838 | 0.308 |  | #4 | 100 | 100 | 100 | 100 | 0 | 0 | 0
[17 empty] | 102 | 100 | 3-3-3-5 | #3 | #5 | 110 | 7 | 102 | 4833 | 0.245 |  | #3 | 110 | 110 | 110 | 110 | 0 | 1
[17 empty] | 103 | 110 | 2-2-2-4 | #2 | #4 | 125 | 8 | 103 | 6087 | 0.194 |  | #2 | 125 | 125 | 130 | 125 | 0 | 0
[17 empty] | 104 | 125 | 1-1-1-3 | #1 | #3 | 150 | 9 | 104 | 7579 | 0.154 |  | #1 | 150 | 150 | 150 | 150 | 0 | 0
[17 empty] | 105 | 150 | 1/0-1/0-1/0-2 | #1/0 | #2 | 175 | 10 | 105 | 9473 | 0.122 |  | #1/0 | 175 | 175 | 175 | 175 | 0 | 0 | 0
[17 empty] | 106 | 175 | 2/0-2/0-2/0-1 | #2/0 | #1 | 200 | 11 | 106 | 11703 | 0.0967 |  | #2/0 | 200 | 200 | 200 | 200 | 0 | 0 | 0
[17 empty] | 107 | 200 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 225 | 12 | 107 | 14410 | 0.0766 |  | #3/0 | 225 | 225 | 225 | 225 | 0 | 0
[17 empty] | 108 | 225 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 250 | 13 | 108 | 17483 | 0.0608 |  | #4/0 | 250 | 250 | 260 | 250 | 0 | 0 |  | 1
[17 empty] | 109 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 109 | EXCEED | EXCEED
[17 empty] | 102 |  | 3-3-3-5 | #3 | #5 | 110 | 7 | 102 | 4833 | 0.245
[19 empty] | SER CABLE |  |  |  |  | SER CABLE
[19 empty] | 3- | #3 | CU |  |  | 3-#3 CU
[19 empty] | 1- | #5 | GND |  |  | 1-#5 GND
4-COND W/GND SER CABLE AL
AMPACITY TABLE
[14 empty] | AMPS | 109 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | AL |  | AWG | AL | AL | AL
[17 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 |  | #6 | 40 | 50 | 60
[17 empty] | 101 | 50 | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 |  | #4 | 55 | 65 | 75
[17 empty] | 102 | 65 | 2-2-2-2-4 | #2 | #4 | 100 | 8 | 102 | 3740 | 0.319 |  | #2 | 100 | 100 | 100 | 100 | 0 | 0
[17 empty] | 103 | 100 | 1-1-1-1-3 | #1 | #3 | 110 | 9 | 103 | 4699 | 0.253 |  | #1 | 110 | 110 | 115 | 110 | 0 | 1
[17 empty] | 104 | 110 | 1/0-1/0-1/0-1/0-2 | #1/0 | #2 | 125 | 10 | 104 | 5876 | 0.201 |  | #1/0 | 125 | 125 | 135 | 125 | 0 | 0
[17 empty] | 105 | 125 | 2/0-2/0-2/0-2/0-1 | #2/0 | #1 | 150 | 11 | 105 | 7373 | 0.159 |  | #2/0 | 150 | 150 | 150 | 150 | 0 | 0
[17 empty] | 106 | 150 | 3/0-3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 175 | 12 | 106 | 9243 | 0.126 |  | #3/0 | 175 | 175 | 175 | 175 | 0 | 0
[17 empty] | 107 | 175 | 4/0-4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 200 | 13 | 107 | 11409 | 0.1 |  | #4/0 | 200 | 200 | 205 | 200 | 0 | 0
[17 empty] | 108 | 200 | 250-250-250-250-3/0 | #250 | #3/0 | 225 | 14 | 108 | 13236 | 0.0847 |  | #250 | 225 | 225 | 230 | 225 | 0 | 0
[17 empty] | 109 | 225 | 300-300-300-300-4/0 | #300 | #4/0 | 250 | 15 | 109 | 15495 | 0.0707 |  | #300 | 250 | 250 | 255 | 250 | 0 | 0 |  | 1
[17 empty] | 110 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 103 |  | 1-1-1-1-3 | #1 | #3 | 110 | 9 | 103 | 4699 | 0.253
[19 empty] | SER CABLE |  |  |  |  | SER CABLE
[19 empty] | 4- | #1 | AL |  |  | 4-#1 AL
[19 empty] | 1- | #3 | GND |  |  | 1-#3 GND
3-COND W/GND ROMEX CABLE CU
AMPACITY TABLE
[14 empty] | AMPS | 109 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS
[19 empty] | AWG |  |  | AL | NUMBER |  |  | CU |  | AWG | CU | CU | CU
[17 empty] | 100 | 0 | 6-6-6-6 | #6 | #10 | 65 | 5 | 100 | 2433 | 0.491 |  | #6 | 55 | 65 | 75
[17 empty] | 101 | 65 | 4-4-4-4 | #4 | #8 | 85 | 6 | 101 | 3838 | 0.308 |  | #4 | 70 | 85 | 95
[17 empty] | 102 | 85 | 2-2-2-2 | #2 | #8 | 115 | 7 | 102 | 4833 | 0.194 |  | #2 | 95 | 115 | 130
[17 empty] | 103 | 115 | EXCEED | EXCEED | EXCEED | 115 | EXCEED | 103 | EXCEED | EXCEED
[28 empty] | #2 | 95 | 115 | 130
[17 empty] | 102 |  | 2-2-2-2 | #2 | #8 | 115 | 7 | 102 | 4833 | 0.194
[19 empty] | ROMEX |  |  |  |  | ROMEX
[19 empty] | 3- | #2 | CU |  |  | 3-#2 CU
[19 empty] | 1- | #8 | GND |  |  | 1-#8 GND
3-COND W/GND MC CABLE AL
AMPACITY TABLE
[14 empty] | AMPS | 109 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | AL |  | AWG | AL | AL | AL
[17 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 |  | #6 | 40 | 50 | 60
[17 empty] | 101 | 50 | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 |  | #4 | 55 | 65 | 75
[17 empty] | 102 | 65 | 2-2-2-4 | #2 | #4 | 100 | 8 | 102 | 3734 | 0.319 |  | #2 | 100 | 100 | 100 | 100 | 0 | 0
[17 empty] | 103 | 100 | 1-1-1-4 | #1 | #4 | 110 | 9 | 103 | 4686 | 0.253 |  | #1 | 110 | 110 | 115 | 110 | 0 | 1
[17 empty] | 104 | 110 | 1/0-1/0-1/0-4 | #1/0 | #4 | 125 | 10 | 104 | 5852 | 0.201 |  | #1/0 | 125 | 125 | 135 | 125 | 0 | 0
[17 empty] | 105 | 125 | 2/0-2/0-2/0-4 | #2/0 | #4 | 150 | 11 | 105 | 7327 | 0.159 |  | #2/0 | 150 | 150 | 150 | 150 | 0 | 0
[17 empty] | 106 | 150 | 3/0-3/0-3/0-4 | #3/0 | #4 | 175 | 12 | 106 | 9077 | 0.126 |  | #3/0 | 175 | 175 | 175 | 175 | 0 | 0
[17 empty] | 107 | 175 | 4/0-4/0-4/0-2 | #4/0 | #2 | 200 | 13 | 107 | 11185 | 0.1 |  | #4/0 | 200 | 200 | 205 | 200 | 0 | 0
[17 empty] | 108 | 200 | 250-250-250-2 | #250 | #2 | 225 | 14 | 108 | 12797 | 0.0847 |  | #250 | 225 | 225 | 230 | 225 | 0 | 0
[17 empty] | 109 | 225 | 350-350-350-1 | #300 | #1 | 250 | 16 | 109 | 16795 | 0.0605 |  | #350 | 250 | 250 | 280 | 250 | 0 | 0 |  | 1
[17 empty] | 110 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 103 |  | 1-1-1-4 | #1 | #4 | 110 | 9 | 103 | 4686 | 0.253
[19 empty] | MC CABLE |  |  |  |  | MC CABLE
[19 empty] | 3- | #1 | AL |  |  | 3-#1 AL
[19 empty] | 1- | #4 | GND |  |  | 1-#4 GND
4-COND W/GND MC CABLE AL
AMPACITY TABLE
[14 empty] | AMPS | 109 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | AL |  | AWG | AL | AL | AL
[17 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 |  | #6 | 40 | 50 | 60
[17 empty] | 101 | 50 | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 |  | #4 | 55 | 65 | 75
[17 empty] | 102 | 65 | 2-2-2-2-4 | #2 | #4 | 100 | 8 | 102 | 3734 | 0.319 |  | #2 | 100 | 100 | 100 | 100 | 0 | 0
[17 empty] | 103 | 100 | 1-1-1-1-4 | #1 | #4 | 110 | 9 | 103 | 4686 | 0.253 |  | #1 | 110 | 110 | 115 | 110 | 0 | 1
[17 empty] | 104 | 110 | 1/0-1/0-1/0-1/0-4 | #1/0 | #4 | 125 | 10 | 104 | 5852 | 0.201 |  | #1/0 | 125 | 125 | 135 | 125 | 0 | 0
[17 empty] | 105 | 125 | 2/0-2/0-2/0-2/0-4 | #2/0 | #4 | 150 | 11 | 105 | 7327 | 0.159 |  | #2/0 | 150 | 150 | 150 | 150 | 0 | 0
[17 empty] | 106 | 150 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 175 | 12 | 106 | 9077 | 0.126 |  | #3/0 | 175 | 175 | 175 | 175 | 0 | 0
[17 empty] | 107 | 175 | 4/0-4/0-4/0-4/0-2 | #4/0 | #2 | 200 | 13 | 107 | 11185 | 0.1 |  | #4/0 | 200 | 200 | 205 | 200 | 0 | 0
[17 empty] | 108 | 200 | 250-250-250-250-1 | #250 | #1 | 225 | 14 | 108 | 12797 | 0.0847 |  | #250 | 225 | 225 | 230 | 225 | 0 | 0
[17 empty] | 109 | 225 | 350-350-350-350-1/0 | #350 | #1/0 | 250 | 16 | 109 | 16795 | 0.0605 |  | #350 | 250 | 250 | 280 | 250 | 0 | 0 |  | 1
[17 empty] | 110 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 103 |  | 1-1-1-1-4 | #1 | #4 | 110 | 9 | 103 | 4686 | 0.253
[19 empty] | MC CABLE |  |  |  |  | MC CABLE
[19 empty] | 4- | #1 | AL |  |  | 4-#1 AL
[19 empty] | 1- | #4 | GND |  |  | 1-#4 GND
3-COND W/GND MC CABLE CU
AMPACITY TABLE
[14 empty] | AMPS | 109 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | CU |  | AWG | CU | CU | CU
[17 empty] | 100 | 0 | 4-4-4-8 | #4 | #8 | 100 | 6 | 100 | 3830 | 0.308 |  | #4 | 100 | 100 | 100 | 100 | 0 | 0 | 0
[17 empty] | 101 | 100 | 3-3-3-6 | #3 | #6 | 110 | 7 | 101 | 4820 | 0.245 |  | #3 | 110 | 110 | 110 | 110 | 0 | 1
[17 empty] | 102 | 110 | 2-2-2-6 | #2 | #6 | 125 | 8 | 102 | 5989 | 0.194 |  | #2 | 125 | 125 | 130 | 125 | 0 | 0
[17 empty] | 103 | 125 | 1-1-1-6 | #1 | #6 | 150 | 9 | 103 | 7454 | 0.154 |  | #1 | 150 | 150 | 150 | 150 | 0 | 0
[17 empty] | 104 | 150 | 1/0-1/0-1/0-6 | #1/0 | #6 | 175 | 10 | 104 | 9210 | 0.122 |  | #1/0 | 175 | 175 | 175 | 175 | 0 | 0 | 0
[17 empty] | 105 | 175 | 2/0-2/0-2/0-6 | #2/0 | #6 | 200 | 11 | 105 | 11245 | 0.0967 |  | #2/0 | 200 | 200 | 200 | 200 | 0 | 0 | 0
[17 empty] | 106 | 200 | 3/0-3/0-3/0-4 | #3/0 | #4 | 225 | 12 | 106 | 13656 | 0.0766 |  | #3/0 | 225 | 225 | 225 | 225 | 0 | 0
[17 empty] | 107 | 225 | 4/0-4/0-4/0-4 | #4/0 | #4 | 250 | 13 | 107 | 16392 | 0.0608 |  | #4/0 | 250 | 250 | 260 | 250 | 0 | 0
[17 empty] | 108 | 250 | 250-250-250-4 | #250 | #4 | 300 | 14 | 108 | 18311 | 0.0515 |  | #250 | 300 | 300 | 300 | 300 | 0 | 0 | 0
[17 empty] | 109 | 300 | 350-350-350-3 | #350 | #3 | 350 | 16 | 109 | 22646 | 0.0367 |  | #350 | 350 | 350 | 350 | 350 | 0 | 0 |  | 1
[17 empty] | 110 | 350 | EXCEED | EXCEED | EXCEED | 350 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 101 |  | 3-3-3-6 | #3 | #6 | 110 | 7 | 101 | 4820 | 0.245
[19 empty] | MC CABLE |  |  |  |  | MC CABLE
[19 empty] | 3- | #3 | CU |  |  | 3-#3 CU
[19 empty] | 1- | #6 | GND |  |  | 1-#6 GND
4-COND W/GND MC CABLE CU
AMPACITY TABLE
[14 empty] | AMPS | 109 |  | ROW | LOOKUP | WIRE | WIRE | NEUTRAL | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | CU |  | AWG | CU | CU | CU
[17 empty] | 100 | 0 | 4-4-4-4-8 | #4 | #8 | 100 | 6 | 100 | 3830 | 0.308 |  | #4 | 100 | 100 | 100 | 100 | 0 | 0 | 0
[17 empty] | 101 | 100 | 3-3-3-3-6 | #3 | #6 | 110 | 7 | 101 | 4820 | 0.245 |  | #3 | 110 | 110 | 110 | 110 | 0 | 1
[17 empty] | 102 | 110 | 2-2-2-2-6 | #2 | #6 | 125 | 8 | 102 | 5989 | 0.194 |  | #2 | 125 | 125 | 130 | 125 | 0 | 0
[17 empty] | 103 | 125 | 1-1-1-1-6 | #1 | #6 | 150 | 9 | 103 | 7454 | 0.154 |  | #1 | 150 | 150 | 150 | 150 | 0 | 0
[17 empty] | 104 | 150 | 1/0-1/0-1/0-1/0-6 | #1/0 | #6 | 175 | 10 | 104 | 9210 | 0.122 |  | #1/0 | 175 | 175 | 175 | 175 | 0 | 0 | 0
[17 empty] | 105 | 175 | 2/0-2/0-2/0-2/0-6 | #2/0 | #6 | 200 | 11 | 105 | 11245 | 0.0967 |  | #2/0 | 200 | 200 | 200 | 200 | 0 | 0 | 0
[17 empty] | 106 | 200 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 225 | 12 | 106 | 13656 | 0.0766 |  | #3/0 | 225 | 225 | 225 | 225 | 0 | 0
[17 empty] | 107 | 225 | 4/0-4/0-4/0-4/0-4 | #4/0 | #4 | 250 | 13 | 107 | 16392 | 0.0608 |  | #4/0 | 250 | 250 | 260 | 250 | 0 | 0
[17 empty] | 108 | 250 | 250-250-250-250-4 | #250 | #4 | 300 | 14 | 108 | 18311 | 0.0515 |  | #250 | 300 | 300 | 300 | 300 | 0 | 0 | 0
[17 empty] | 109 | 300 | 350-350-350-350-3 | #350 | #3 | 350 | 16 | 109 | 22646 | 0.0367 |  | #350 | 350 | 350 | 350 | 350 | 0 | 0 |  | 1
[17 empty] | 110 | 350 | EXCEED | EXCEED | EXCEED | 350 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 101 |  | 3-3-3-3-6 | #3 | #6 | 110 | 7 | 101 | 4820 | 0.245
[19 empty] | MC CABLE |  |  |  |  | MC CABLE
[19 empty] | 4- | #3 | CU |  |  | 4-#3 CU
[19 empty] | 1- | #6 | GND |  |  | 1-#6 GND

## Inport (hidden)
| ERROR | PANEL | PANEL | BREAKER | FAULT | LENGTH | CONDUIT | WIRE 1 | WIRE 2 | WIRE 3 | WIRE 4 | VD % | 1-PHASE | SQUARE | APPLIANCE | LAUNDRY | NUMBER | RANGE | NUMBER | DRYER | WATER | WATER | HEAT | HEAT | HEAT | HEAT | HEAT | HEAT | MISC | APP COUNT | APP KVA | APP COUNT | APP KVA
|  | NAME | PHASE | SIZE | CURRENT |  | CABLE | [6 empty] | FOOTAGE | CIRCUITS | CIRCUITS | OF | KVA | OF | KVA | HEATER | HEATER | 1 | 2 | 3 | 4 | 5 | 6 | LOADS | YES | YES | NO | NO
[17 empty] | RANGES |  | DRYERS |  | NUMBER | KVA
1 | 0 | SP1 | 1 | 60A-2P | 6.6 K | 25' | 1- SER CABLE | 3-#4 AL | 1-#6 GND |  |  | 0.4 % VD
| 0 | SP2 | 1 | 60A-2P | 6.6 K | 25' | 1- SER CABLE | 3-#4 AL | 1-#6 GND |  |  | 0.4 % VD
| 0 | SP3 | 1 | 60A-2P | 6.6 K | 25' | 1- SER CABLE | 3-#4 AL | 1-#6 GND |  |  | 0.4 % VD
| 0 | SP4 | 1 | 60A-2P | 6.6 K | 25' | 1- SER CABLE | 3-#4 AL | 1-#6 GND |  |  | 0.4 % VD
| 0 | SP5 | 1 | 60A-2P | 6.6 K | 25' | 1- SER CABLE | 3-#4 AL | 1-#6 GND |  |  | 0.4 % VD
| 0 | SP6 | 1 | 60A-2P | 6.6 K | 25' | 1- SER CABLE | 3-#4 AL | 1-#6 GND |  |  | 0.4 % VD

## Update (hidden)
ITEM | SP1 | SP1 | SP1 | SP2 | SP2 | SP3 | SP3 | SP4 | SP4 | SP5 | SP5 | SP6 | SP6
| OUT | BACK | UPDATE | BACK | UPDATE | BACK | UPDATE | BACK | UPDATE | BACK | UPDATE | BACK | UPDATE
HI VOLTS | 240 | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0 | 240 | 0
LOW VOLTS | 120 | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | 120 | 0
PHASE | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0
AFC | 15818 | 15818 | 0 | 15818 | 0 | 15818 | 0 | 15818 | 0 | 15818 | 0 | 15818 | 0
VD CALCS | YES | YES | 0 | YES | 0 | YES | 0 | YES | 0 | YES | 0 | YES | 0
FAULT CALCS | YES | YES | 0 | YES | 0 | YES | 0 | YES | 0 | YES | 0 | YES | 0
CODE YEAR | 2008 | 2008 | 0 | 2008 | 0 | 2008 | 0 | 2008 | 0 | 2008 | 0 | 2008 | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0

## Export (hidden)
CONDUIT | WIRE 1 | WIRE 2 | WIRE 3 | WIRE 4
CABLE
1-1 1/4'' EMT | 2-#1 THHN AL | 1-#4 THHN AL (N) | 1-#4 AL GND